## Table 1
GROWATT VPP COMMUNICATION PROTOCOL OF INVERTER | [34 empty] | Version V2.03 Date 2025.9.1
Copyright © Shenzhen Growatt New Energy Co., Ltd. 2024. All rights reserved. No part of this document may be reproduced, stored in a retrieval system, or transmitted, in any form or by any means, be it electronic, mechanical, photographic, magnetic or otherwise, without the prior written per-mission of Shenzhen Growatt New Energy Co., Ltd.
SHENZHEN GROWATT NEW ENERGY
Address: Telephone: website: | [7 empty] | 4-13/Building A, Sino-German(Europe) industrial Park, Hangcheng Ave, Bao'an District, Shenzhen, China 400-931-9122 www.growatt.com ¦ service@ginverter.com
Version Record
|  | Index |  |  |  |  | Version | [6 empty] | Change content | [21 empty] | Author | [7 empty] | Date
|  | 1 |  |  |  |  | V1.01 | [6 empty] | First Republic | [21 empty] | Meilin Luo | [7 empty] | 2021-02-19
|  | 2 |  |  |  |  | V1.02 | [6 empty] | (1) Add MOD-XH MID-XH DTC (2) Increase the input register PV parameter information to PV1~PV16 (3) Maintain register battery side parameter fields: hold 31200-31300 Increase battery system battery increase information: Number of battery clusters, number of modules (PACKs) under a single cluster, rated battery power, and rated battery capacity (4) Chapter 30500~30799 of the new safety parameter hold 30500~30799 in the register (reserved) (5) Basic information holding registers 30060-30081 add software version information for inverters, batteries, and meters (6) Work status information Status information 31007-31008 Add fault and alarm sub codes (7) Add 32000~32099 100 registers for energy storage system summary information | [21 empty] | Jian Li | [7 empty] | 2023-08-16
|  | 3 |  |  |  |  | V1.03 | [6 empty] | (1) Holding register System Order Control Information add 30115 SYN enable (2) Holding register AC Power control set parameter add 30155~30157 EPS off-grid enable, EPS off-grid frequency, EPS off-grid voltage, 30203~30204 Export Limitation Failure time/EMS communicating fail time, EMS communicating fail enable，30154 change the remark (3) Holding register Battery Power Control Set Information add 30475 off-grid discharge cut off SOC, 30496~30499 battery charge stop voltage, battery discharge stop voltage, battery charge max current, battery discharge max current， 30400~30403 battery charge max power turn into reserved, 30405 name turn into on-grid discharge stop SOC (4) Input register add 31300~31399 Battery Information 2, 31400~31499 Battery Information 3, 31500~31599 Battery Information 4 (5) Input register working status information 31000 Working state of energy storage machine remark: 5: PV online & battery offline ,6: battery online & PV offline (or offline) (6) Holding register30227~30228 Module Rated Voltage, Module Rated Cap change register number to 1 | [21 empty] | Ziqi Kang | [7 empty] | 2023-12-06
|  | 4 |  |  |  |  | V2.0 | [6 empty] | (1) Holding register30500~30999 safety parameter separately sorted out a document and this protocol together with the VPP protocol, common maintenance | [21 empty] | Ziqi Kang | [7 empty] | 2024-03-22
(2) Holding register 30084 change number from 15 to 16 (3) Holding register 30157 add the type of Off-grid voltage of WIT, 30201 change register range to [-100,100]，and add some description of logic: 30496~30499 add range limitation, 30162 change the description of range (4) Holding register add 30099 VPP protocol version， 30205 super Export Limitation enable, 30206 Export Limitation feed power change slope, 30207 Export Limitation single ctrl, 30208 Export Limitation Protection Mode (5) Input register 31219 change name to full charge capacity(FCC), 31210 and 31224 reserved (6) Standard Modbus protocol definition add data form of single byte
5 | [5 empty] | V2.01 | [6 empty] | (1) Holding register 30001 SN change the type to UINT16, 30157 EPS off-grid voltage add notes for its range, MIN 7-10KTL-X/X2 and MIC/MIN 2.5-6K TL-X/X2 don’t use the parameters of battery (2) Holding register 30162 power factor turn its range into [0,2000]∪[18000,20000], the default value turn into 20000 (3) Holding register add 30300 battery cluster index (4) Annexed table 3-1 renew the machine type and DTC, attachment 3.3 to 3.6 add power control position diagram, added Export Limitation, remote charge/discharge control, reactive power control schematic diagram | [21 empty] | Ziqi Kang | [7 empty] | 2024-09-20
6 | [5 empty] | V2.03 | [6 empty] | (1) On/off command 30101 add the bypass mode (2) Fix Q 30160 change its maximum from 60 to 70 (3) The default value of Power factor 30162 change from 10000 to 20000 (4) Holding register add 30209-30215 on/off-grid switch and active power control (5) Holding register add 30250-30299 Diesel engine module (6) Holding register add 30301-30305 Peak-shaving module (7) 30404-30406 and 30475, the range of the stop charging /discharging SOC change to [10,100] (8) AC charge enable 30410 add Only AC charging mode (9) Holding register add 30476 TOU default mode, 30477 TOU reset enable (10) Off-grid voltage 30157 replenish the range of different machine, Working state of inverter 31000 change its description (11) Attachment 3.1 update the table 3-1 and 3-5 , add 3.4 the initial logic | [21 empty] | Ziqi Kang | [7 empty] | 2025-08-31
Catalog 1 Introduction 6 1.1 Purpose 6 1.2 Scope 6 1.3 Terms and abbreviations 6 2 Protocol register 8 2.1 Hold register 8 2.2 Input register 19 3 Attachment 25 3.1 Annexed table 25 3.2 Definition of the protocol 30 3.2.1 Standard Modbus protocol definition 30 3.2.2 Command format 30 3.3 Power control position diagram 34 3.4 Export Limitation power control schematic diagram 35 3.5 Remote power control schematic diagram 36 3.6 Reactive power control schematic diagram 37
1 Introduction 1.1 Purpose The purpose of writing this document is to explain the RTU communication protocol of energy storage / inverter products to realize virtual power plant remote dispatching (VPP) in detail. 1.2 Scope For the energy storage / inverter products applicable to the remote dispatching of smart grid, see Annex Table 1 for details. 1.3 Terms and abbreviations
Terms and abbreviations | [14 empty] | Explanation
LCD | [14 empty] | Liquid crystal display
WIFI | [14 empty] | Wireless communication module
LAN | [14 empty] | Local and network
USB | [14 empty] | Universal serial bus
UINT16 | [14 empty] | Unsigned 16 bit shaping (high byte first, low byte last)
UINT32 | [14 empty] | Unsigned 32-bit shaping (high word first, low word last)
INT16 | [14 empty] | Signed 16 bit shaping (high byte first, low byte last)
INT32 | [14 empty] | Signed 32-bit shaping (high word first, low word last)
STR | [14 empty] | String MLD multi-byte
Bitfield16 | [14 empty] | 16Bit wise representation of bit width
Bitfield32 | [14 empty] | 32Bit wise representation of bit width
Register address | [14 empty] | The register address corresponds to a 2-byte message
- | [14 empty] | Not involved
S | [14 empty] | second
RO | [14 empty] | Read only data
RW | [14 empty] | Readable and writable data
WO | [14 empty] | Write data only
DSP | [14 empty] | Digital signal processing controller
ENSE | [14 empty] | Energy storage integrated cabinet
EMS | [14 empty] | Energy Management System
PCS | [14 empty] | Power Conversion System
Terms and abbreviations | [14 empty] | Explanation
BMS | [14 empty] | Battery Management System
VPP | [14 empty] | Virtual Power Plant
AC | [14 empty] | Alternating Current
DC | [14 empty] | Direct Current
PV | [14 empty] | Photovoltaic
SN | [14 empty] | Serial Number
2 Protocol register 2.1 Hold register
N O. |  |  |  | Parameter name | [9 empty] | Rea d/w rite |  |  | Type | [6 empty] | Unit |  |  |  |  | Address |  |  |  | Num ber |  |  |  | Range
Basic Parameter:30000~30099
1 |  |  |  | Equipment type (DTC) | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30000 |  |  |  | 1 |  |  |  | See Table 3-1
2 |  |  |  | SN | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30001 |  |  |  | 15 |  |  |  | -
3 |  |  |  | Rated power (Pn) | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30016 |  |  |  | 2 |  |  |  | -
4 |  |  |  | Maximum active power (Pmax) | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30018 |  |  |  | 2 |  |  |  | -
5 |  |  |  | Maximum reactive power (Qmax fed into the grid) | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1VAR |  |  |  |  | 30020 |  |  |  | 2 |  |  |  | -
6 |  |  |  | Maximum reactive power (Qmax absorptiOn-grid) | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1VAR |  |  |  |  | 30022 |  |  |  | 2 |  |  |  | -
7 |  |  |  | Maximum apparent power (Smax) | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1VA |  |  |  |  | 30024 |  |  |  | 2 |  |  |  | -
8 |  |  |  | Rated charging and discharging power of BDC | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30026 |  |  |  | 2 |  |  |  | -
9 |  |  |  | PV input maximum power | [9 empty] | RO |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30028 |  |  |  | 2 |  |  |  | -
10 |  |  |  | Battery type | [9 empty] | RO |  |  | UINT8 | [6 empty] | - |  |  |  |  | 30030 |  |  |  | 1 |  |  |  | 0: lead acid battery 1: lithium battery
11 |  |  |  | Reserve | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30031 |  |  |  | 29 |  |  |  | -
Inverter Version Information
12 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30060 |  |  |  | 1 |  |  |  | Example: MOD-
XH:DN
13 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30061 |  |  |  | 1 |  |  |  | Example: MOD- XH:AA
14 |  |  |  | Version Num 1 | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30062 |  |  |  | 1 |  |  |  | Example: MOD-XH:09
15 |  |  |  | Version Num 2 | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30063 |  |  |  | 1 |  |  |  | Example: MOD-XH:51
16 |  |  |  | Version Num 3 | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30064 |  |  |  | 1 |  |  |  | Example: MOD-XH:01
17 |  |  |  | M3 Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30065 |  |  |  | 1 |  |  |  | Example: MOD-XH: ZB
18 |  |  |  | M3 Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30066 |  |  |  | 1 |  |  |  | Example: MOD-XH: DC
19 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30067 |  |  |  | 1 |  |  |  | Example: MOD-XH:12
Energy Storage Battery Version Information
20 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30068 |  |  |  | 1 |  |  |  | Example:APX5.0: WA
21 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30069 |  |  |  | 1 |  |  |  | Example:APX5.0: AA
22 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30070 |  |  |  | 1 |  |  |  | Example:APX5.0: 09
23 |  |  |  | DSP2 Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30071 |  |  |  | 1 |  |  |  | Example:APX5.0: VC
24 |  |  |  | DSP2 Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30072 |  |  |  | 1 |  |  |  | Example:APX5.0: BA
25 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30073 |  |  |  | 1 |  |  |  | Example:APX5.0: 09
26 |  |  |  | BCU Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30074 |  |  |  | 1 |  |  |  | Example:APX5.0: QB
27 |  |  |  | BCU Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30075 |  |  |  | 1 |  |  |  | Example:APX5.0: AA
28 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30076 |  |  |  | 1 |  |  |  | Example:APX5.0: 09
29 |  |  |  | M3 Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30077 |  |  |  | 1 |  |  |  | Example:APX5.0: ZE
30 |  |  |  | M3 Software Version Name | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30078 |  |  |  | 1 |  |  |  | Example:APX5.0: BA
31 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | Digit |  |  |  |  | 30079 |  |  |  | 1 |  |  |  | Example:APX5.0: 09
Meter Version Information
32 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30080 |  |  |  | 1 |  |  |  | Example: ZO
33 |  |  |  | Machine Model | [9 empty] | RO |  |  | UINT16 | [6 empty] | ASCII |  |  |  |  | 30081 |  |  |  | 1 |  |  |  | Example: AA
34 |  |  |  | Version Num | [9 empty] | RO |  |  | UINT16 | [6 empty] | 1 |  |  |  |  | 30082 |  |  |  | 1 |  |  |  | Example: 02
35 |  |  |  | Reserved | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30083 |  |  |  | 1 |  |  |  | Reserved
VPP Protocol Version Information
36 |  |  |  | Reserved | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30084 |  |  |  | 15 |  |  |  | Reserved
37 |  |  |  | VPP Protocol Version | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30099 |  |  |  | 1 |  |  |  | 200 represents V2.00, 201 represents V2.01, others are similar
System Order Control Information:30100~30149
38 |  |  |  | Control authority | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30100 |  |  |  | 1 |  |  |  | 0: not enabled 1: Enable Default value: 0 Using this protocol needs to enable this register
39 |  |  |  | On off command | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30101 |  |  |  | 1 |  |  |  | 0: power off 1: power on 9: bypass Default value: 1 Not storage
40 |  |  |  | Country / region number | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30102 |  |  |  | 1 |  |  |  | See Table 3-5
41 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30103 |  |  |  | 1 |  |  |  | -
42 |  |  |  | System time | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30104 |  |  |  | 6 |  |  |  | See table 3-6
43 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT32 | [6 empty] | - |  |  |  |  | 30110 |  |  |  | 2 |  |  |  | -
44 |  |  |  | Mailing address | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30112 |  |  |  | 1 |  |  |  | [1, 255] Default value: 1
45 |  |  |  | Communication baud rate | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30113 |  |  |  | 1 |  |  |  | 0:9600 bps 1:38400 bps Default value: 0
46 |  |  |  | Reserved | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30114 |  |  |  | 1 |  |  |  | -
47 |  |  |  | SYN enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30115 |  |  |  | 1 |  |  |  | Off-grid box enable 0: not enabled 1: enable Default value: 0
48 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30116 |  |  |  | 34 |  |  |  | -
AC Power Control Set Parameter:30150~30299
49 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30150 |  |  |  | 1 |  |  |  | -
50 |  |  |  | Active power percentage derating | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30151 |  |  |  | 1 |  |  |  | Power limit percentage: [0,100] Default value: 100
51 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30152 |  |  |  | 2 |  |  |  | -
52 |  |  |  | Static active power limitation | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30154 |  |  |  | 1 |  |  |  | Power limit percent: [0,100] Default value: 100 Actual active power is the less one between Active power percentage derating and Static active power limitation Not storage
53 |  |  |  | EPS off-grid enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30155 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
54 |  |  |  | EPS off-grid frequency | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.01Hz |  |  |  |  | 30156 |  |  |  | 1 |  |  |  | 0:50Hz 1:60Hz Default value: 0
55 |  |  |  | EPS off-grid voltage (3) | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30157 |  |  |  | 1 |  |  |  | Default value: 0
56 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30158 |  |  |  | 2 |  |  |  | -
57 |  |  |  | Fix Q | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30160 |  |  |  | 1 |  |  |  | Power limit percentage: [0,70] Default value: 0
58 |  |  |  | Reactive power mode | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30161 |  |  |  | 1 |  |  |  | 0: PF=1 1: Pf value setting 4: Lagging reactive power (+) 5: Leading reactive power (-) Default value: 0 When the battery is discharged or not connected, negative value indicates captive reactive power and positive value indicates inductive reactive power. When charging , the situation is Reverse See Appendix 3.6 for the logic
59 |  |  |  | Power factor | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30162 |  |  |  | 1 |  |  |  | [0, 2000] ∪ [18000,20000] Default value:20000 Actual power factor = (set value - 10000) * 0.0001
60 |  |  |  | Reserve | [9 empty] | RW |  |  | INT16 | [6 empty] | % |  |  |  |  | 30163 |  |  |  | 1 |  |  |  | -
61 |  |  |  | Reserve (reactive power curve) | [9 empty] | - |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30164 |  |  |  | 36 |  |  |  | -
62 |  |  |  | Export Limitation Enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30200 |  |  |  | 1 |  |  |  | 0: not enabled 1: single machine Export Limitation enable Default value: 0
See Appendix 3.3 and 3.4 for the logic
63 |  |  |  | Export Limitation power Rate | [9 empty] | RW |  |  | INT16 | [6 empty] | % |  |  |  |  | 30201 |  |  |  | 1 |  |  |  | [-100，100] Default value: 0 Positive value is export , negative value is import
64 |  |  |  | Export Limitation Failure power Rate | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30202 |  |  |  | 1 |  |  |  | [0，100] Default value: 0
65 |  |  |  | EMS Communicating Failure Time | [9 empty] | RW |  |  | UINT16 | [6 empty] | S |  |  |  |  | 30203 |  |  |  | 1 |  |  |  | Export Limitation Failure time [1,300] Default value: 30
66 |  |  |  | EMS Communication Failure Enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30204 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
67 |  |  |  | Super Export Limitation enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30205 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
68 |  |  |  | Export Limitation change slope | [9 empty] | RW |  |  | UINT16 | [6 empty] | *0.01% Pn/s |  |  |  |  | 30206 |  |  |  | 1 |  |  |  | [1,20000] Default value: 27
69 |  |  |  | Export Limitation single phase control enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30207 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
70 |  |  |  | Export Limitation protection mode （2） | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30208 |  |  |  | 1 |  |  |  | 0: Default mode 1: Combine control mode 2: software control mode 3: hardware control mode Default value: 0
71 |  |  |  | Automatic on/off-grid switch enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30209 |  |  |  | 1 |  |  |  | 0: Automatic 1: Manual Default value: 0
72 |  |  |  | On/odd grid set | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30210 |  |  |  | 1 |  |  |  | When manual mode: Modify on-grid or
off-grid or engine mode 0: on-grid mode 1: off-grid mode 2: diesel engine mode Default value: 0 Can be set only when 30209 is enabled
73 |  |  |  | Active power R | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30211 |  |  |  | 1 |  |  |  | [0, rated power/3]
74 |  |  |  | Active power S | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30212 |  |  |  | 1 |  |  |  | [0, rated power/3]
75 |  |  |  | Active power T | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30213 |  |  |  | 1 |  |  |  | [0, rated power/3]
76 |  |  |  | Single phase control of Active power enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30214 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
77 |  |  |  | AC charge power max limitation | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30215 |  |  |  | 1 |  |  |  | [0, rated power] Default value: No limit Used only when 30410 is enabled
78 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30216 |  |  |  | 34 |  |  |  | -
Diesel Engine Control Module: 30250~30299
79 |  |  |  | Diesel Engine rated power | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30250 |  |  |  | 1 |  |  |  | [0, 10000] Default value:inverter rated power
80 |  |  |  | Diesel Engine charge power | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30251 |  |  |  | 1 |  |  |  | [0, 10000] Default value:inverter rated power
81 |  |  |  | Diesel Engine enable | [9 empty] | RW |  |  | BOOL | [6 empty] | - |  |  |  |  | 30252 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
82 |  |  |  | Off-grid Diesel Engine start SOC | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30253 |  |  |  | 1 |  |  |  | [0, 100] Default value:20
83 |  |  |  | Off-grid Diesel Engine stop SOC | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30254 |  |  |  | 1 |  |  |  | [0, 100] Default value:50
84 |  |  |  | Diesel Engine preheat time | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30255 |  |  |  | 1 |  |  |  | [0, 3600] Default value:60
85 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30256 |  |  |  | 44 |  |  |  | -
Battery Power Control Set Information:30300~30499(4）
86 |  |  |  | Battery cluster index | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30300 |  |  |  | 1 |  |  |  | [0,3] If the register is set to x, then read/write information [30400,30406], [30474,30475], and [30496,30499] belong to cluster x Default value: 0, which indicates that the current battery information applies to all battery clusters
87 |  |  |  | Demand management enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30301 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
88 |  |  |  | Demand management export power limitation | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30302 |  |  |  | 1 |  |  |  | [0, rated power] Default value: No limit
89 |  |  |  | Demand management import power limitation | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1KW |  |  |  |  | 30303 |  |  |  | 1 |  |  |  | [0, rated power] Default value: No limit
90 |  |  |  | Peak-shaving back up power SOC | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30304 |  |  |  | 1 |  |  |  | [0, 100] Default value:50
91 |  |  |  | Peak-shaving enable | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30305 |  |  |  | 1 |  |  |  | 0: not enabled 1: enable Default value: 0
92 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30306 |  |  |  | 94 |  |  |  | -
93 |  |  |  | Reserve(Battery max charging | [9 empty] | RW |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30400 |  |  |  | 2 |  |  |  | Not used
power)
94 |  |  |  | Reserve (Battery max discharging power) | [9 empty] | RW |  |  | UINT32 | [6 empty] | 0.1W |  |  |  |  | 30402 |  |  |  | 2 |  |  |  | Not used
95 |  |  |  | Charging cut off SOC | [9 empty] | RW |  |  | UINT8 | [6 empty] | % |  |  |  |  | 30404 |  |  |  | 1 |  |  |  | [10，100] Default value: 100
96 |  |  |  | On-grid discharge cut off SOC | [9 empty] | RW |  |  | UINT8 | [6 empty] | % |  |  |  |  | 30405 |  |  |  | 1 |  |  |  | [10，100] Default value: 10
97 |  |  |  | Load first discharge cut off SOC(1) | [9 empty] | RW |  |  | UINT8 | [6 empty] | % |  |  |  |  | 30406 |  |  |  | 1 |  |  |  | [10，100] Default value: 10
98 |  |  |  | Remote power control enable | [9 empty] | RW |  |  | UINT8 | [6 empty] | - |  |  |  |  | 30407 |  |  |  | 1 |  |  |  | 0: not enabled 1: Enable Default value: 0 Not storage See Appendix 3.5 for the logic
99 |  |  |  | Remote power control charging time | [9 empty] | RW |  |  | UINT16 | [6 empty] | min |  |  |  |  | 30408 |  |  |  | 1 |  |  |  | 0: unlimited time 1 ~ 1440min: control the power duration according to the set time Default value: 0 Not storage
100 |  |  |  | Remote charge and discharge power | [9 empty] | RW |  |  | INT16 | [6 empty] | - |  |  |  |  | 30409 |  |  |  | 1 |  |  |  | [-100，100] Positive: charging Negative: discharge Default value: 0 Not storage
101 |  |  |  | AC charging enable | [9 empty] | RW |  |  | UINT8 | [6 empty] | - |  |  |  |  | 30410 |  |  |  | 1 |  |  |  | 0: not enabled 1: Enable AC charge, PV charging first 2: Enable AC charge, AC charging first Default value: 0
102 |  |  |  | Charging and discharging in | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30411 |  |  |  | 61 |  |  |  | See Table 3-2 30412~30471 are
|  |  |  | different periods (20 sections) | [32 empty] | time setting, default value: 0
103 |  |  |  | Reserve | [9 empty] | RO |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30472 |  |  |  | 2 |  |  |  | -
104 |  |  |  | Actual control value of charging and discharging power | [9 empty] | RO |  |  | INT16 | [6 empty] | - |  |  |  |  | 30474 |  |  |  | 1 |  |  |  | [-100, 100] Positive: charging Negative: discharge
105 |  |  |  | Off-grid discharge cut off SOC | [9 empty] | RW |  |  | UINT16 | [6 empty] | % |  |  |  |  | 30475 |  |  |  | 1 |  |  |  | [10, 100] Default value:10
106 |  |  |  | TOU default mode | [9 empty] | RW |  |  | UINT8 | [6 empty] | - |  |  |  |  | 30476 |  |  |  | 1 |  |  |  | For the TOU and remote power control mode, the settings for the time outside the periods that was set 0: load first 1: battery first 2: grid first Default value: 0
107 |  |  |  | TOU reset enable | [9 empty] | RW |  |  | UINT8 | [6 empty] | - |  |  |  |  | 30477 |  |  |  | 1 |  |  |  | [0, 1] After enabled, when setting the time periods next time, all the original time period information will be completely cleared Default value: 0
108 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30478 |  |  |  | 18 |  |  |  | -
109 |  |  |  | Battery charge stop voltage | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1V |  |  |  |  | 30496 |  |  |  | 1 |  |  |  | Lead-acid battery used only [0,15000] Distinguished by voltage level: 127V: 6500 227V: 10000
Others: 8000
110 |  |  |  | Battery discharge stop voltage | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1V |  |  |  |  | 30497 |  |  |  | 1 |  |  |  | Lead-acid battery used only [0,15000] Distinguished by voltage level: 127V: 3800 227V: 7500 Others: 6500
111 |  |  |  | Battery max charge current | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1A |  |  |  |  | 30498 |  |  |  | 1 |  |  |  | Lead-acid battery used only [0,2000] Default value : 1500
112 |  |  |  | Battery max discharge current | [9 empty] | RW |  |  | UINT16 | [6 empty] | 0.1A |  |  |  |  | 30499 |  |  |  | 1 |  |  |  | Lead-acid battery used only [0,2000] Default value : 1500
Safety Information:30500~30999
113 |  |  |  | See details in GROWATT INVERTER VPP COMMUNICATIO N PROTOCOL & SAFETY PARAMETERS | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 30500 |  |  |  | 500 |  |  |  | -
Energy Storage System Information:32000~32099
114 |  |  |  | Reserve | [9 empty] | RW |  |  | UINT16 | [6 empty] | - |  |  |  |  | 32000 |  |  |  | 100 |  |  |  | -
Notes: all RW parameters will be stored in EEPROM, except for the special notes “Not Storage”. High frequency writing is not supported. (1) Load first discharge cut off SOC (30406) is only used by SPH/SPA type. (2):SPH/SPA/WIT/WIS do not use Export Limitation protection mode (30208), the description of each mode is as follows. 0: Default mode, when the meter is disconnected or communication fails, the inverter will limit the output power to the Export Limitation Failure Power; When the output power is larger than the Export Limitation Power, the inverter will report an error and be off-grid. 1: Combine control mode, when the meter is disconnected or communication fails, the inverter will report an error and be off-grid within 5s; When the output power is larger than the
Export Limitation Power, the inverter will be off-grid after 15s. 2: Software control mode, when the meter is disconnected or communication fails, the inverter will reduce the output power to the Export Limitation Failure Power within 15s; When the output power is larger than the Export Limitation Power, the inverter reduces the output power to the set Export Limitation Failure Power within 15s. 3: Hardware control mode, when the meter is disconnected or communication fails, the inverter will report an error and be off-grid within 5s; When the output power is larger than the Export Limitation Power, the inverter will be off-grid within 5s. (3) Different model ranges of EPS off-grid voltage (30157) are shown in the following table:
[5 empty] | Machine Type | [19 empty] | EPS off-grid voltage
[5 empty] | WIT/WIS | [19 empty] | 0:230V 1:208V 2:240V 3:220V 4:127V 5:277V 6:254V
[5 empty] | MOD-XH\MID-XH MOD\MID-HU | [19 empty] | 0:230V 1:208V 2:240V 3:220V
[5 empty] | SPH/SPA | [19 empty] | 0:230V 1:208V 2:240V
[5 empty] | others | [19 empty] | Not used
2.2 Input register
N O. |  |  |  | Parameter name | [8 empty] | Rea d/w rite |  |  | Type | [5 empty] | Unit | [6 empty] | Address |  |  |  | Num ber |  |  |  | Range
Working status information:31000~31009
1 |  |  |  | Working state of inverter | [8 empty] | RO |  |  | UINT16 | [5 empty] | 1 | [6 empty] | 31000 |  |  |  | 1 |  |  |  | 0: standby 1: self-test 2: reserved 3: fault 4: upgrade 5: PV online &
battery offline & On-grid 6: PV online (or offline) & battery online & On-grid 7: PV online & battery online & off-grid 8: PV offline & battery online & off-grid 9: bypass
2 |  |  |  | Battery working status | [8 empty] | RO |  |  | UINT16 | [5 empty] | 1 | [6 empty] | 31001 |  |  |  | 1 |  |  |  | 0: battery standby 1: Battery disconnected 2: battery charging operation 3: battery discharge operation 4: fault 5: upgrade
3 |  |  |  | Priority of work | [8 empty] | RO |  |  | UINT16 | [5 empty] | 1 | [6 empty] | 31002 |  |  |  | 1 |  |  |  | 0: load first 1: Battery first 2: grid first
4 |  |  |  | Reserve | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31003 |  |  |  | 2 |  |  |  | -
5 |  |  |  | Fault code | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31005 |  |  |  | 1 |  |  |  | See Table 3-3
6 |  |  |  | Fault sub code | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31006 |  |  |  | 1 |  |  |  | See Table 3-3
7 |  |  |  | Alarm code | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31007 |  |  |  | 1 |  |  |  | See Table 3-4
8 |  |  |  | Alarm sub code | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31008 |  |  |  | 1 |  |  |  | See Table 3-4
9 |  |  |  | Reserve | [8 empty] | RO |  |  | UINT16 | [12 empty] | 31009 |  |  |  | 1 |  |  |  | -
PV Parameter:31010~31099
10 |  |  |  | PV1 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31010 |  |  |  | 1 |  |  |  | -
11 |  |  |  | PV1 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31011 |  |  |  | 1 |  |  |  | -
12 |  |  |  | PV2 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31012 |  |  |  | 1 |  |  |  | -
13 |  |  |  | PV2 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31013 |  |  |  | 1 |  |  |  | -
14 |  |  |  | PV3 voltage | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1V | [6 empty] | 31014 |  |  |  | 1 |  |  |  | -
15 |  |  |  | PV3 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31015 |  |  |  | 1 |  |  |  | -
16 |  |  |  | PV4 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31016 |  |  |  | 1 |  |  |  | -
17 |  |  |  | PV4 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31017 |  |  |  | 1 |  |  |  | -
18 |  |  |  | PV5 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31018 |  |  |  | 1 |  |  |  | -
19 |  |  |  | PV5 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31019 |  |  |  | 1 |  |  |  | -
20 |  |  |  | PV6 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31020 |  |  |  | 1 |  |  |  | -
21 |  |  |  | PV6 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31021 |  |  |  | 1 |  |  |  | -
22 |  |  |  | PV7 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31022 |  |  |  | 1 |  |  |  | -
23 |  |  |  | PV7 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31023 |  |  |  | 1 |  |  |  | -
24 |  |  |  | PV8 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31024 |  |  |  | 1 |  |  |  | -
25 |  |  |  | PV8 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31025 |  |  |  | 1 |  |  |  | -
26 |  |  |  | PV9 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31026 |  |  |  | 1 |  |  |  | -
27 |  |  |  | PV9 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31027 |  |  |  | 1 |  |  |  | -
28 |  |  |  | PV10 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31028 |  |  |  | 1 |  |  |  | -
29 |  |  |  | PV10 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31029 |  |  |  | 1 |  |  |  | -
30 |  |  |  | PV11 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31030 |  |  |  | 1 |  |  |  | -
31 |  |  |  | PV11 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31031 |  |  |  | 1 |  |  |  | -
32 |  |  |  | PV12 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31032 |  |  |  | 1 |  |  |  | -
33 |  |  |  | PV12 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31033 |  |  |  | 1 |  |  |  | -
34 |  |  |  | PV13 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31034 |  |  |  | 1 |  |  |  | -
35 |  |  |  | PV13 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31035 |  |  |  | 1 |  |  |  | -
36 |  |  |  | PV14 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31036 |  |  |  | 1 |  |  |  | -
37 |  |  |  | PV14 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31037 |  |  |  | 1 |  |  |  | -
38 |  |  |  | PV15 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31038 |  |  |  | 1 |  |  |  | -
39 |  |  |  | PV15 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31039 |  |  |  | 1 |  |  |  | -
40 |  |  |  | PV16 voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31040 |  |  |  | 1 |  |  |  | -
41 |  |  |  | PV16 current | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31041 |  |  |  | 1 |  |  |  | -
42 |  |  |  | Reserve | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31042 |  |  |  | 16
43 |  |  |  | PV input power | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1W | [6 empty] | 31058 |  |  |  | 2 |  |  |  | -
44 |  |  |  | Reserve | [8 empty] | RO |  |  | UINT32 | [5 empty] | - | [6 empty] | 31060 |  |  |  | 40 |  |  |  | -
AC Information:31100~31199
45 |  |  |  | Active power | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1W | [6 empty] | 31100 |  |  |  | 2 |  |  |  | Positive: export to grid Negative: import from grid
46 |  |  |  | Reactive power | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1VA | [6 empty] | 31102 |  |  |  | 2 |  |  |  | -
47 |  |  |  | Reserve | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31104 |  |  |  | 1 |  |  |  | -
48 |  |  |  | Grid frequency | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.01Hz | [6 empty] | 31105 |  |  |  | 1 |  |  |  | -
49 |  |  |  | Grid voltage / line AB voltage | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.1V | [6 empty] | 31106 |  |  |  | 1 |  |  |  | When the output mode is L/N, the voltage and current are grid voltage and grid current respectively
50 |  |  |  | BC line voltage of power grid | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.1V | [6 empty] | 31107 |  |  |  | 1 |  |  |  | -
51 |  |  |  | CA line voltage of power grid | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.1V | [6 empty] | 31108 |  |  |  | 1 |  |  |  | -
52 |  |  |  | Grid current / A phase current of grid | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31109 |  |  |  | 1 |  |  |  | -
53 |  |  |  | Phase B current of grid | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31110 |  |  |  | 1 |  |  |  | -
54 |  |  |  | Phase C current of grid | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1A | [6 empty] | 31111 |  |  |  | 1 |  |  |  | -
55 |  |  |  | Meter power | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1W | [6 empty] | 31112 |  |  |  | 2 |  |  |  | Positive: import from grid Negative: export to grid
56 |  |  |  | Inverter temperature | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1℃ | [6 empty] | 31114 |  |  |  | 1 |  |  |  | [-400，1250]
57 |  |  |  | Reserve | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31115 |  |  |  | 1 |  |  |  | -
58 |  |  |  | Reserve | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31116 |  |  |  | 1 |  |  |  | -
59 |  |  |  | Reserve | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31117 |  |  |  | 1 |  |  |  | -
60 |  |  |  | Power to user daily | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31118 |  |  |  | 2 |  |  |  | -
61 |  |  |  | Total power to user | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31120 |  |  |  | 2 |  |  |  | -
62 |  |  |  | Power to grid daily | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31122 |  |  |  | 2 |  |  |  | -
63 |  |  |  | Total power to grid | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31124 |  |  |  | 2 |  |  |  | -
64 |  |  |  | Reserved | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31126 |  |  |  | 74 |  |  |  | -
Battery Information 1 (BDC and BMS containing):31200~31299
65 |  |  |  | Charge/dischar | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1W | [6 empty] | 31200 |  |  |  | 2 |  |  |  | Positive: charging
|  |  |  | ge power | [32 empty] | Negative: discharge
66 |  |  |  | Daily charge of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31202 |  |  |  | 2 |  |  |  | -
67 |  |  |  | Cumulative charge of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31204 |  |  |  | 2 |  |  |  | -
68 |  |  |  | Daily discharge capacity of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31206 |  |  |  | 2 |  |  |  | -
69 |  |  |  | Cumulative discharge of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1KWH | [6 empty] | 31208 |  |  |  | 2 |  |  |  | -
70 |  |  |  | Maximum allowable charging power of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1W | [6 empty] | 31210 |  |  |  | 2 |  |  |  | -
71 |  |  |  | Maximum allowable discharge power of battery | [8 empty] | RO |  |  | UINT32 | [5 empty] | 0.1W | [6 empty] | 31212 |  |  |  | 2 |  |  |  | -
72 |  |  |  | Battery voltage | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1V | [6 empty] | 31214 |  |  |  | 1 |  |  |  | -
73 |  |  |  | Battery current | [8 empty] | RO |  |  | INT32 | [5 empty] | 0.1A | [6 empty] | 31215 |  |  |  | 2 |  |  |  | Positive: charging Negative: discharge
74 |  |  |  | SOC | [8 empty] | RO |  |  | UINT8 | [5 empty] | % | [6 empty] | 31217 |  |  |  | 1 |  |  |  | [0，100]
75 |  |  |  | SOH | [8 empty] | RO |  |  | UINT8 | [5 empty] | % | [6 empty] | 31218 |  |  |  | 1 |  |  |  | [0，100]
76 |  |  |  | Battery capacity rating (FCC) | [8 empty] | RO |  |  | UINT32 | [5 empty] | AH | [6 empty] | 31219 |  |  |  | 2 |  |  |  | -
77 |  |  |  | Reserved | [8 empty] | RO |  |  | UINT32 | [5 empty] | - | [6 empty] | 31221 |  |  |  | 2 |  |  |  | Reserved for Battery remaining capacity (RM)
78 |  |  |  | Battery environmental temperature | [8 empty] | RO |  |  | INT16 | [5 empty] | 0.1℃ | [6 empty] | 31223 |  |  |  | 1 |  |  |  | [-400，1250]
79 |  |  |  | Reserved | [8 empty] | RO |  |  | INT16 | [5 empty] | - | [6 empty] | 31224 |  |  |  | 1 |  |  |  | Reserved for Maximum battery temperature
80 |  |  |  | Cluster Sum | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31225 |  |  |  | 1 |  |  |  | -
81 |  |  |  | Single Cluster Module Number | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31226 |  |  |  | 1 |  |  |  | -
82 |  |  |  | Module Rated Voltage | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.1V | [6 empty] | 31227 |  |  |  | 1 |  |  |  | -
83 |  |  |  | Module Rated Cap | [8 empty] | RO |  |  | UINT16 | [5 empty] | 0.1AH | [6 empty] | 31228 |  |  |  | 1 |  |  |  | -
84 |  |  |  | Reserve | [8 empty] | RO |  |  | UINT16 | [5 empty] | - | [6 empty] | 31229 |  |  |  | 71 |  |  |  | -
Battery Information 2 (BDC and BMS containing):31300~31399
85 |  |  |  | 31300~31399 refer to 31200~31299
Battery Information 3 (BDC and BMS containing):31400~31499
86 |  |  |  | 31400~31499 refer to 31200~31299
Battery Information 4 (BDC and BMS containing):31500~31599
87 |  |  |  | 31500~31599 refer to 31200~31299
3 Attachment 3.1 Annexed table Table 3-1 DTC code description
| Type | [12 empty] | Full name | [22 empty] | DTC code
| SPH/SPA | [12 empty] | SPH 3000-6000TL BL | [22 empty] | 3501
[14 empty] | SPH 3000-6000TL BL-UP | [22 empty] | 3502
[14 empty] | SPH 3000-6000TL HU | [22 empty] | 3503
[14 empty] | SPH 3000-6000TL HUB | [22 empty] | 3504
[14 empty] | SPA 1000-3000TL BL | [22 empty] | 3701
[14 empty] | SPA 3000TL BL-UP | [22 empty] | 3735
[14 empty] | SPA 3000-6000TL AU | [22 empty] | 3715
[14 empty] | SPA 3000-6000TL AUB | [22 empty] | 3716
[14 empty] | SPA 4-10KTL3 BH-UP | [22 empty] | 3725
[14 empty] | SPH 4-10KTL3 BH-UP | [22 empty] | 3601
| MIN-XH | [12 empty] | MIN 2500-6000TL-XH/XH2/XHE/XA | [22 empty] | 5100
| MOD-XH/MID-XH | [12 empty] | MOD 3-10KTL3-XH/BP、 MID 11-30KTL3-XH、 MID 8-15KTL3-XHL/JP | [22 empty] | 5400
| MOD/MID-HU | [12 empty] | MOD 3-15KTL3-HU、 MID 33-50KTL3-HU | [22 empty] | 5401
| WIT/WIS | [12 empty] | WIS 100K-AM; WIT 50-100K-H/HE/HU/A/AE/AU; WIT 50-100K-H/HE/HU/A/AE/AU-US; WIT 28-55K-H/HE/HU/A/AE/AU-US L2 | [22 empty] | 5600
[14 empty] | WIT29.9-50K-XHU | [22 empty] | 5601
[14 empty] | WIS 210K | [22 empty] | 5800
[14 empty] | WIS 215K-AM | [22 empty] | 5801
| MIC/MIN-X | [12 empty] | MIC 600-3300TL-X/X2/X2(Pro); MIN 2500-6000TL-X/X2/X2(Pro)/X2(Pro.E); | [22 empty] | 5200
[14 empty] | MIN 7-10KTL-X/X2/X2(E) | [22 empty] | 5201
| MOD/MID/MAC-X | [12 empty] | MID 17-25KTL3-X; MID 20-30KTL3-X2; MID 25-30KTL3-X2 Pro/X2 Pro.E MID 33-50KTL3-X2/X2 Pro/X2 Pro.E MID 30-40KTL3-X; | [22 empty] | 5001
MID 33-36KTL3-X(Pro.E); MID 3-33KTL3-X3;
[14 empty] | MOD 3-15KTL3-X; MOD 3-15KTL3-X2(Pro); MOD 12-20KTL3-X2; MOD 12-20KTL3-X2(E); MOD 3-33KTL3-X3; | [22 empty] | 5002
[14 empty] | MAC 30-70KTL3-X; MAC 15-36KTL3-XL; MAC 50-70KTL3-X2; MAC 30-36KTL3-XL2; | [22 empty] | 5003
| MAX/MAX-X | [12 empty] | MAX 50-100KTL3 LV/MV | [22 empty] | 5000
[14 empty] | MAX 175-253KTL3-X HV | [22 empty] | 5500
[14 empty] | MAX 80-150KTL3-X LV/MV、 MAX 100-150KYL3-X2 LV/MV | [22 empty] | 5501
[14 empty] | MAX 320-350KTL3-X | [22 empty] | 5502
Note: MIN-X&MOD/MID/MAC-X&MAX/MAX-X do not use the battery and energy storage related registers.
Table 3-2 Description of parameter format of charging and discharging by time interval
Description | [17 empty] | Data type | [9 empty] | Unit | [5 empty] | Value range
Number of time periods | [17 empty] | UINT8 | [9 empty] | - | [5 empty] | [0, 20] Default value: 0, the following are the same
Start time of period 1 | [17 empty] | UINT16 | [9 empty] | Min | [5 empty] | [0, 1440], relative to the number of minutes at 0 o’clock every day, the start time less than end time
End time of period 1 | [17 empty] | UINT16 | [9 empty] | Min
Charging and discharging power of period 1 | [17 empty] | INT16 | [9 empty] | % | [5 empty] | [-100,100] Positive: charging Negative: discharge
Start time of period 2 | [17 empty] | UINT16 | [9 empty] | Min | [5 empty] | [0, 1440], relative to the number of minutes at 0 o’clock every day, the start time less than end time
End time of period 2 | [17 empty] | UINT16 | [9 empty] | Min
Charging and discharging power in period 2 | [17 empty] | INT16 | [9 empty] | % | [5 empty] | [-100,100]
……
Start time of period 19 | [17 empty] | UINT16 | [9 empty] | Min | [5 empty] | [0, 1440], relative to the number of minutes at 0 o’clock every day, the start time less than end time
End time of period 19 | [17 empty] | UINT16 | [9 empty] | Min
Charge discharge power of period 19 | [17 empty] | INT16 | [9 empty] | % | [5 empty] | [-100,100]
Start time of period 20 | [17 empty] | UINT16 | [9 empty] | Min | [5 empty] | [0, 1440], relative to the number of minutes at 0 o’clock every day, the start time less than the end time
End time of period 20 | [17 empty] | UINT16 | [9 empty] | Min
Charge discharge power of period 20 | [17 empty] | INT16 | [9 empty] | % | [5 empty] | [-100,100]
Note: The time range setting requires 0x10 to write multiple hold register function codes; the 20-time piece ranges must be mutually exclusive; otherwise, the setting fails.
Table 3-3 Fault codes (Reference product fault list)
Serial number | [9 empty] | Fault code | [6 empty] | Auxiliary code | [12 empty] | Fault name | [7 empty] | Causes or measures
Table 3-4 Alarm codes (Reference product fault list)
Serial number | [9 empty] | Fault code | [6 empty] | Auxiliary code | [12 empty] | Fault name | [7 empty] | Causes or measures
Table 3-5 Country / region numbers
Number | [11 empty] | Standard | [19 empty] | Applicable countries
0 | [11 empty] | SA_NULL
1 | [11 empty] | SA_VDE0126 | [19 empty] | Germany
2 | [11 empty] | SA_G99 | [19 empty] | Britain
3 | [11 empty] | SA_AS4777 | [19 empty] | Australia
4 | [11 empty] | SA_CEI0_21 | [19 empty] | Italy
5 | [11 empty] | SA_SPAIN | [19 empty] | Spain
6 | [11 empty] | SA_GREECE_CONTINENT | [19 empty] | The Greek continent
7 | [11 empty] | SA_N4105 | [19 empty] | Germany
8 | [11 empty] | SA_G98 | [19 empty] | Britain
9 | [11 empty] | SA_IRELAND | [19 empty] | Ireland
10 | [11 empty] | SA_CQC_2013 | [19 empty] | China
11 | [11 empty] | SA_EN50438 | [19 empty] | Poland/Norway/Turkey/Switzerland
12 | [11 empty] | SA_IEC62116&61727 | [19 empty] | Hungary
13 | [11 empty] | SA_BELGIUM | [19 empty] | Belgium
14 | [11 empty] | SA_MEA | [19 empty] | Thailand
15 | [11 empty] | SA_PEA | [19 empty] | Thailand
16 | [11 empty] | SA_NEWZWALAND | [19 empty] | New Zealand
17 | [11 empty] | SA_CQC_PLANT | [19 empty] | China
18 | [11 empty] | SA_INDIA | [19 empty] | India
19 | [11 empty] | SA_DEMARK_DK1 | [19 empty] | Denmark
20 | [11 empty] | SA_SWEDEN | [19 empty] | Sweden
21 | [11 empty] | SA_NORWAY | [19 empty] | Norway
22 | [11 empty] | SA_QUEENSLAND | [19 empty] | Queensland
23 | [11 empty] | SA_FRANCE | [19 empty] | France
24 | [11 empty] | SA_KOREA_60HZ | [19 empty] | the republic of Korea
25 | [11 empty] | SA_BRAZIL | [19 empty] | Brazil
26 | [11 empty] | SA_CEI0_16 | [19 empty] | Italy
27 | [11 empty] | SA_DEWA | [19 empty] | Dubai
28 | [11 empty] | SA_CHILE | [19 empty] | Chile
29 | [11 empty] | SA_ARGENTINA | [19 empty] | Argentina
30 | [11 empty] | SA_N4110_BDEW | [19 empty] | Germany
31 | [11 empty] | SA_TAIWAN_VPC | [19 empty] | Taiwan
32 | [11 empty] | SA_DEMARK_DK2 | [19 empty] | Denmark
33 | [11 empty] | SA_CQC_2018 | [19 empty] | China
34 | [11 empty] | SA_DEMARK_TR3_3_1 | [19 empty] | Denmark
35 | [11 empty] | SA_POLAND | [19 empty] | Poland
36 | [11 empty] | SA_TAIWAN_TPC | [19 empty] | Taiwan Electric Power Bureau
37 | [11 empty] | SA_IEEE1547_1 | [19 empty] | North America
38 | [11 empty] | SA_BRAZIL_240V | [19 empty] | Brazil
39 | [11 empty] | SA_EN50549 | [19 empty] | Europe
40 | [11 empty] | SA_AU_VICTORIA | [19 empty] | Victoria
41 | [11 empty] | SA_AU_WESTERN | [19 empty] | Western Australia 1
42 | [11 empty] | SA_AU_HORIZON | [19 empty] | Western Australia 2
43 | [11 empty] | SA_AU_AUSGRID | [19 empty] | New South Wales 1
44 | [11 empty] | SA_AU_ENDEAVOUR | [19 empty] | New South Wales 2
45 | [11 empty] | SA_AU_ERGONENERGY | [19 empty] | Queensland 1
46 | [11 empty] | SA_AU_ENERGEX | [19 empty] | Queensland 2
47 | [11 empty] | SA_AU_SANETWORK | [19 empty] | Nan ao electric
48 | [11 empty] | SA_US_UL1741 | [19 empty] | North America
49 | [11 empty] | SA_US_RULE21 | [19 empty] | North America
50 | [11 empty] | SA_US_RULE14_HECO | [19 empty] | North America
51 | [11 empty] | SA_NRS097 | [19 empty] | South Africa
52 | [11 empty] | SA_TUNISIA | [19 empty] | Tunisia
53 | [11 empty] | SA_PRC_EAST | [19 empty] | North America
54 | [11 empty] | SA_PRC_WEST | [19 empty] | North America
55 | [11 empty] | SA_PRC_QUEBEC | [19 empty] | North America
56 | [11 empty] | SA_AUSTRIA | [19 empty] | Austria
57 | [11 empty] | SA_ESTONIA | [19 empty] | Estonia
58 | [11 empty] | SA_NI_G98 | [19 empty] | Northern Ireland
59 | [11 empty] | SA_NI_G99 | [19 empty] | Northern Ireland
60 | [11 empty] | SA_INDIA_KERALA | [19 empty] | India Kerala
61 | [11 empty] | SA_EN50549_2 | [19 empty] | Europe
62 | [11 empty] | SA_NETHER_LAND | [19 empty] | Netherland
63 | [11 empty] | SA_CZECH | [19 empty] | Czech
64 | [11 empty] | SA_VIETNAM_EVN | [19 empty] | Vietnam
65 | [11 empty] | SA_GREECE_ISLAND | [19 empty] | Greece island
66 | [11 empty] | SA_DEMARK_TR331_DK2 | [19 empty] | Denmark
67 | [11 empty] | SA_LIETUANIA | [19 empty] | Lithuania
68 | [11 empty] | SA_LATVIJA | [19 empty] | Latvia
69 | [11 empty] | SA_SPAIN_NTS | [19 empty] | Spain
70 | [11 empty] | SA_ISRAEL | [19 empty] | Israel
71 | [11 empty] | SA_PAKISTAN | [19 empty] | Pakistan
73 | [11 empty] | SA_US_NEWYORK | [19 empty] | North America
74 | [11 empty] | SA_US_ISONE | [19 empty] | North America
75 | [11 empty] | SA_US_LUMA | [19 empty] | North America
76 | [11 empty] | SA_JP_JET | [19 empty] | Japan
77 | [11 empty] | SA_MALAYSIA | [19 empty] | Malaysia
78 | [11 empty] | SA_US_PHI | [19 empty] | North America
79 | [11 empty] | SA_US_SMECO | [19 empty] | North America
80 | [11 empty] | SA_US_PE | [19 empty] | North America
81 | [11 empty] | SA_US_BGE | [19 empty] | North America
82 | [11 empty] | SA_SAUDI | [19 empty] | Saudi
83 | [11 empty] | SA_URUGUAY | [19 empty] | Uruguay
84 | [11 empty] | SA_DEMARK_DK1_TYPEB | [19 empty] | Denmark
85 | [11 empty] | SA_DEMARK_DK2_TYPEB | [19 empty] | Denmark
86 | [11 empty] | SA_DEMARK_TR331_DK1_TYPEB | [19 empty] | Denmark
87 | [11 empty] | SA_DEMARK_TR331_DK2_TYPEB | [19 empty] | Denmark
88 | [11 empty] | SA_CROATIA | [19 empty] | Croatia
89 | [11 empty] | SA_ROMANIA | [19 empty] | Romania
90 | [11 empty] | SA_SWITZERLAND | [19 empty] | Switzerland
91 | [11 empty] | SA_GBT34120-2023 | [19 empty] | China
92 | [11 empty] | SA_HUNGARY | [19 empty] | Hungary
Table 3-6 system time setting
Description | [12 empty] | Data type | [12 empty] | Unit | [9 empty] | Value range
Year | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [12, 99] Default value: 12
Month | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [1, 12] Default value: 1
Day | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [1, 31] Default value: 1
Time | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [0, 24] Default value: 0
Minute | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [0, 59] Default value: 0
Second | [12 empty] | UINT8 | [12 empty] | - | [9 empty] | [0, 59] Default value: 0
3.2 Definition of the protocol
3.2.1 Standard Modbus protocol definition Data format:
Address | [12 empty] | Function | [13 empty] | Data | [10 empty] | CRC Check
8 bits | [12 empty] | 8 bits | [13 empty] | N*8 bits | [10 empty] | 16 bits
The valid slave address range is 0 - 254 decimal. The address range assigned to each slave device is 1-254. 0 is a broadcast address. Each hold or input register is a 16 bit (two bytes) unsigned integer. Each byte consists of 8-bit binary characters, and each 8-bit byte in the packet contains two 4-bit hexadecimal characters (0~9, A~F). The data format of each byte (10 bits) is: 1 start bit + 8 data bits + 1 stop bit, and the transmission process is shown in the figure (each byte is sent in order from left to right).
Start bits | [8 empty] | 1 |  |  | 2 |  |  |  | 3 |  |  |  |  | 4 | [5 empty] | 5 |  |  |  |  | 6 |  |  | 7 |  |  |  | 8 |  |  |  |  | Stop bits
3.2.2 Command format
(1）Function code 0x03 read hold register Send Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 3
Starting Address Hi | [26 empty] | 0
Starting Address Lo | [26 empty] | 6B
No. of Points Hi | [26 empty] | 0
No. of Points Lo | [26 empty] | 3
Error Check(LRC or CRC) | [26 empty] | -
Response Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 3
Byte Count | [26 empty] | 6
Data Hi | [26 empty] | 2
Data Lo | [26 empty] | 2B
Data Hi | [26 empty] | 0
Data Lo | [26 empty] | 0
Data Hi | [26 empty] | 0
Data Lo | [26 empty] | 64
Error Check(LRC or CRC) | [26 empty] | -
Response error:11 0x80 ¦ 0x03 Error number CRC (Error number is a byte)
(2) Function code 0x04 read input register Send Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 4
Starting Address Hi | [26 empty] | 0
Starting Address Lo | [26 empty] | 8
No. of Points Hi | [26 empty] | 0
No. of Points Lo | [26 empty] | 1
Error Check(LRC or CRC) | [26 empty] | -
Response Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 4
Byte Count | [26 empty] | 2
Data Hi | [26 empty] | 0
Data Lo | [26 empty] | 0A
Error Check(LRC or CRC) | [26 empty] | -
Response error:11 0x80 ¦ 0x04 Error number CRC (Error number is a byte)
(3) Function code 0x06 preset single register Send Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 6
Register Address Hi | [26 empty] | 0
Register Address Lo | [26 empty] | 1
Preset Data Hi | [26 empty] | 0
Preset Data Lo | [26 empty] | 3
Error Check(LRC or CRC) | [26 empty] | -
Response Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 6
Register Address Hi | [26 empty] | 0
Register Address Lo | [26 empty] | 1
Preset Data Hi | [26 empty] | 0
Preset Data Lo | [26 empty] | 3
Error Check(LRC or CRC) | [26 empty] | -
Response error:11 0x80¦0x06 Error number CRC (Error number is a byte)
(4) Function code 0x10: preset multiple registers Send Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 10
Starting Address Hi | [26 empty] | 0
Starting Address Lo | [26 empty] | 1
No. of Registers Hi | [26 empty] | 0
No. of Registers Lo | [26 empty] | 2
Byte Count | [26 empty] | 4
Data Hi | [26 empty] | 0
Data Lo | [26 empty] | 0A
Data Hi | [26 empty] | 1
Data Lo | [26 empty] | 2
Error Check(LRC or CRC) | [26 empty] | -
Response Message:
Field Name | [26 empty] | Example(HEX)
Slave Address | [26 empty] | 11
Function | [26 empty] | 10
Starting Address Hi | [26 empty] | 0
Starting Address Lo | [26 empty] | 1
No. of Registers Hi | [26 empty] | 0
No. of Registers Lo | [26 empty] | 2
Error Check(LRC or CRC) | [26 empty] | -
Response Error:11 0x80¦0x10 Error number CRC (Error number is a byte)
Error codes:
Description | [14 empty] | Code | [15 empty] | Meaning
Illegal function | [14 empty] | 0x01 | [15 empty] | 1 write undefined function code 2 write reading only registers 3 read writing only registers
Illegal data address | [14 empty] | 0x02 | [15 empty] | 1 write undefined address 2 read undefined address 3 read data crossing multi-groups
Illegal data | [14 empty] | 0x03 | [15 empty] | 1 write data over prescribed scope
Checkout fault | [14 empty] | 0x08 | [15 empty] | 1 CRC checkout error
3.3 Snmmary of schematic diagrams 3.3.1 Power control position diagram The following figure shows the limits of the Export Limitation power, Export Limitation Failure Power Rate, and battery charging/discharging power percentage.
AC side：control point of Actual control power of charging/discharging (WIT/WIS used)
AC side：control point of Export Limitation Failure power
[5 empty] | Battery(DC) side： control point of Actual control power of charging/discharging (SPH/SPA/MOD/MID/MI N-XH used) | [33 empty] | Meter side:control side of Export limitation power
BATTERY LOAD
The parameters involved in the figure above can be read from the following registers:
|  | Parameter name | [22 empty] | Holding register(setting value) | [11 empty] | Input register(actual value)
|  | Actual control value of charging/ discharging power | [22 empty] | 30474 | [11 empty] | /
|  | Export Limitation Power Rate | [22 empty] | 30201 | [11 empty] | /
|  | Export Limitation Failure Power Rate | [22 empty] | 30202 | [11 empty] | /
|  | Charge/discharge power Pbat | [22 empty] | / | [11 empty] | 31200
|  | Active power Po | [22 empty] | / | [11 empty] | 31100
|  | Meter power Pm | [22 empty] | / | [11 empty] | 31112
3.3.2 Export Limitation power control schematic diagram
Do not limit export power
Use Export limitation power(30201) to limit AC side power Po
Use export limitation failure power(30202) to limit AC side power Po
3.3.3 Remote power control schematic diagram Remote power control 30407~30476 logical diagram are as follows.
Remote power control charging time （30408）= 0? N In Remote power control N charging time(30408)? Y
Actual control value of charging/ discharging power(30474) = Remote chargIng/dischargIng power(30409)
Y
Remote chargIng/dischargIng power(30409)＞0 then battery first, 0 then grid first
Charging/ discharging power(30412-30471)＞0 then battery first, 0 then grid first
3.3.4 Reactive power control schematic diagram Reactive power control 30160~30162 logical diagram are as follows.
Set Reactive power mode(30161)
[11 empty] | Y |  |  |  |  | Y
Y
[25 empty] | Set register 30160, output reactive power percent is capacitive when the battery is discharged or not connected, and is inductive when charging | [14 empty] | Set register 30160, output reactive power percent is inductive when the battery is discharged or not connected, and is capacitive when charging
Set register 30162,change PF to control reactive power
PF default value is 1
3.4 Logic of first time opening When the protocol control permission is enabled for the first time, some parameters will synchronize with the corresponding parameter values of the RTU protocol. This logic is executed only when the inverter is turned on for the first time. The parameters to be synchronized are the following registers:
|  |  | Register address | [17 empty] | Parameter name
|  |  | 30101 | [17 empty] | On off command
|  |  | 30115 | [17 empty] | SYN enable
|  |  | 30151 | [17 empty] | Active power percentage derating
|  |  | 30155 | [17 empty] | EPS off-grid enable
|  |  | 30156 | [17 empty] | EPS off-grid frequency
|  |  | 30157 | [17 empty] | EPS off-grid voltage
|  |  | 30160 | [17 empty] | Fix Q
|  |  | 30161 | [17 empty] | Reactive power mode
|  |  | 30162 | [17 empty] | Power factor
| 30200 | [18 empty] | Export Limitation Enable
| 30201 | [18 empty] | Export Limitation power Rate
| 30202 | [18 empty] | Export Limitation Failure power Rate
| 30203 | [18 empty] | EMS Communicating Failure Time
| 30205 | [18 empty] | Super Export Limitation enable
| 30206 | [18 empty] | Export Limitation change slope
| 30207 | [18 empty] | Export Limitation single phase control enable
| 30208 | [18 empty] | Export Limitation protection mode
| 30404 | [18 empty] | Charging cut off SOC
| 30405 | [18 empty] | On-grid discharge cut off SOC
| 30410 | [18 empty] | AC charging enable
| 30474 | [18 empty] | Actual control value of charging and discharging power
| 30475 | [18 empty] | Off-grid discharge cut off SOC
METER
INVERTER
Export
Pm
Po
Import
PV
~
GRID
Pbat
Start
Dynamic export
limitation
(30200) is open?
N
Y
Meter side power Pm
＞Export limitation
power(30201)?
N
EMS communication
failure enable(30204)is
open?
N
Y
Y
N
Fail time EMS
communication failure time(30203)?
Y
End
Charge/dischar
ge time period
Self-
consumption
Start
Remote power control
enable (30407)is open?
N
Y Remote
charge/discharge
Y
Number of time
periods = 0?
N
Default mode is
Load first, can change by 30476
N
In charging/discharging time
period(30412-30471)?
Y
Actual control value of charging/
discharging power(30474)
=Charging/ discharging
power(30412-30471)
End
Start
30161 is 0?
30161 is 1?
30161 is 4?
30161 is 5?
Y
End