## Table 1
Growatt Inverter Modbus RTU Protocol_II V1.13 2019-1-16 Growatt New Energy CO.,LTD
No. |  |  | Version | [5 empty] | Date | [7 empty] | Notice | [23 empty] | Signature
1 |  |  | V1.00 | [5 empty] | 2017-03-27 | [7 empty] | The first version | [23 empty] | May
2 |  |  | V1.01 | [5 empty] | 2017-04-28 | [7 empty] | Modify max data length to 125 words. Add Inputreg50-52 for line voltage | [23 empty] | May
3 |  |  | V1.02 | [5 empty] | 2017-07-18 | [7 empty] | Add SP storage and offline inverter message Modify Input reg. First and Second group sequence Modify Holding register First group sequence ModigystringPID fault code and warning code Modify fifth and sixth group for Gridfault record | [23 empty] | May
4 |  |  | V1.03 | [5 empty] | 2017-08-02 | [7 empty] | Modify Hybrid Abnoram/Fault/warning bit definition | [23 empty] | Ericxiong
5 |  |  | V1.04 | [5 empty] | 2018-03-29 | [7 empty] | Add Inputing178,179,180,181 for Warning Value1,Warning Value2,Warning Value3 and FaultCode Add Holding240 for aging Check Step Add Inputing112 for INV warn code Add Inputing113 for real Power Percent Add Inputing114 forinv start delay time Add Inputing115 for INVAllFaultCode Add holding267-298 for DSP debugdata address Add Inputing182-197 for DSP debugdata value Add Inputing198 for USB Aging Test OK flag Add Inputing199 for USB Flash Aging Test OK flag Add Inputing200 for ISO check value Add holding299 for ActiveOverloadEnable Add Inputing 201-203 for R、S、T DCI Current Add Inputing204 for PIDBusVolt Add Inputing205 forGFCI Curr Add Inputing 206-227 for APF/SVG information Add holding 300 for SVG/APF mode
6 |  |  | V1.05 | [5 empty] | 2018-06-28 | [7 empty] | Add InputingReg 525~529 for Setting up GPRS IP Address Add HodlingReg 90 as the step to set up GPRS IP Address | [23 empty] | huo.zhao
7 |  |  | V1.06 | [5 empty] | 2018-08-30 | [7 empty] | Add HoldingReg 301 for BDEW LVRT KFactor Add holdingReg 302 for BDEW ZeroCurrentMode Enable Add Inputing228 for 232 Aging Test OK flag Add holding133-147 for new serial number 30 bit | [23 empty] | Yimin.Yang
8 |  |  | V1.07 | [5 empty] | 2018-09-12 | [7 empty] | AddholdingReg 122~123 for export limit set and change Longitude and latitudetoholdingReg 241~242; Add holdingReg 42 for English G100 fail safe set; Union MAX and StorageaboutholdingReg112~115； | [23 empty] | Kin
9 |  |  | V1.08 | [5 empty] | 2018-09-18 | [7 empty] | Add thirteen group 2000~2124 for Storage power’s SPA1-3K | [23 empty] | Kin
10 |  |  | V1.09 | [5 empty] | 2018-10-23 | [7 empty] | Add Holding 303 for SVGAPFEqualRatio Add Holding 304 for Anti-Backflow Failed PowerRate Change Input 206 bit0-7 for SVG/APF Status ， bit8-15 for SVGAPFEqualRatio Change Holding BLVersion to 148-151(old is 118-121) Add houding 118-121 for New model set | [23 empty] | Yimin.Yang
11 |  |  | V1.10 | [5 empty] | 2018-10-29 | [7 empty] | Add holding reg 3000~3124 for TL-X and TL-XH; Add input reg 3000~3249 for TL-X and TL-XH; | [23 empty] | Zhenyuan.li
12 |  |  | V1.11 | [5 empty] | 2018-11-01 | [7 empty] | 1、modify holding reg 122, add set CT select; 2、change new SN reg to holding reg 209~223; 3、change BootVer reg to holding reg 133~136; | [23 empty] | Zhenyuan.li
13 |  |  | V1.12 | [5 empty] | 2018-11-29 | [7 empty] | 1、add Holding 305 for Q load speed 2、add Holding 306 for Parallel Anti-Backflow enable 3、add Input 229 for Fan Fault Bit 4 、 add holding 307 for Anti-Backflow Failure Response Time 5、add holding 310 for GPRS status 6、add Input 230-231 for Output apparent power | [23 empty] | Yimin.Yang
14 |  |  | V1.13 | [5 empty] | 2019-01-16 | [7 empty] | 1、change holding42 for Parallel Anti-Backflow Host NoResponse Flag 2、add holding 308 for Parallel Anti Backflow Power Limit 3、add holding 309 for ISO Check Cmd | [23 empty] | Yimin.Yang
catalog 1 Data format 4 2 Command Format 4 3 Device Message Transmission Mode / Framing 7 4 Register map 8 4.1 Holding Reg 8 4.2 Input Reg 37 5 Set address 81 6 Notice 81
1 Data format Valid slave device addresses are in the range of 0 – 254 decimal. The individual slave devices are assigned addresses in the range of 1 – 254. 0 is the broadcast address It is 16bits (two bytes) unsigned integer for each holding and input register; 2 Command Format Function 3 Read holding register
Response Error: 11 0x80¦0x03 ErrornumCRC(Errornum as a byte) Function 4 Read input register Response Error: 11 0x80¦0x04 ErrornumCRC (Errornum as a byte) Function 6 Preset single register
Response Error: 11 0x80¦0x06 ErrornumCRC (Errornum as a byte) Function 16 Preset multiple register Response Error: 11 0x80¦0x10 ErrornumCRC (Errornum as a byte)
3 Device Message Transmission Mode / Framing RTU Mode When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream. The format for each byte in RTU mode is: Coding System: 8–bit binary, hexadecimal 0–9, A–F Two hexadecimal characters contained in each 8–bit field of the message
Bits per Byte: | [6 empty] | 1 start bit 8 data bits, least significant bit sent first None parity 1 stop bit Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is: Default Baud Rate: 9600 bps Can be set through hold register 22 Minimum CMD period (RS485 Time out): 850ms. Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s; Maximum Data Length Define: Maximum read data length is 125 words in read command; Maximum update data length is 125 words in preset command; Note: Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;
4 Register map It is 16bits (two bytes) unsigned integer for each holding and input register; 4.1 Holding Reg
Registe r NO. |  |  |  | Variable Name | [6 empty] | Description | [10 empty] | Write or not |  |  |  | Value | [5 empty] | Unit |  |  |  |  | Initial value | Note
First group
0 |  |  |  | OnOff | [6 empty] | Remote On/Off . On（1）；Off（0） | [10 empty] | W |  |  |  | 0or1 | [10 empty] | 1 | When PV restart, recover 1.
1 |  |  |  | SaftyFuncEn | [6 empty] | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3: FreqDeratingEnable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc En Bit7~15:reserved | [10 empty] | W |  |  |  | 0 : disable 1: enable | [11 empty] | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA
2 |  |  |  | PF CMD memory state | [6 empty] | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | [10 empty] | W |  |  |  | 0or1 | [10 empty] | 0 | Means these settings will be acting or not when next power on
3 |  |  |  | Active P Rate | [6 empty] | Inverter Max output active power percent | [10 empty] | W |  |  |  | 0-100 or 255 | [5 empty] | % |  |  |  |  | 255 | 255: power is not be limited
4 |  |  |  | Reactive P Rate | [6 empty] | Inverter max output reactive power percent | [10 empty] | W |  |  |  | 0-100 or 255 | [5 empty] | % |  |  |  |  | 255 | 255: power is not be limited
5 |  |  |  | Power factor | [6 empty] | Inverter output power factor’s 10000 times | [10 empty] | W |  |  |  | 0-20000, 0-10000 is underexci ted, other is overexcit ed | [10 empty] | 0
6 |  |  |  | Pmax H | [6 empty] | Normal power (high) | [20 empty] | 0.1VA
7 |  |  |  | Pmax L | [6 empty] | Normal power (low) | [20 empty] | 0.1VA
8 |  |  |  | Vnormal | [6 empty] | Normal work PV voltage | [20 empty] | 0.1V
9 |  |  |  | Fw version H | [6 empty] | Firmware version (high) | [20 empty] | ASCII
10 |  |  |  | Fw version M | [6 empty] | Firmware version (middle)
11 |  |  |  | Fw version L | [6 empty] | Firmware version (low)
12 |  |  |  | Fw version2 H | [6 empty] | Control Firmware version (high) | [20 empty] | ASCII
13 |  |  |  | Fw version2 M | [6 empty] | Control Firmware version (middle) | [20 empty] | ASCII
14 |  |  |  | Fw version2 L | [6 empty] | Control Firmware version (low) | [20 empty] | digital
15 |  |  |  | LCD | [6 empty] | LCD language | [10 empty] | W |  |  |  | 0-5 | [11 empty] | 0: Italian;
|  |  |  | language | [33 empty] | 1: English;
[38 empty] | 2: German |  |  |  |  | ;
[38 empty] | 3: Spanish |  |  |  |  | ;
4: French;
[38 empty] | 5: Chinese |  |  |  |  | ;
16 |  |  |  | CountrySele cted | [6 empty] | Country Selected or not | [10 empty] | W |  |  |  | 0: need to select; 1: have selected
17 |  |  |  | Vpv start | [6 empty] | Input start voltage | [10 empty] | W | [9 empty] | 0.1V
18 |  |  |  | Time start | [6 empty] | Start time | [10 empty] | W | [9 empty] | 1s
19 |  |  |  | RestartDelay Time | [6 empty] | Restart Delay Time after fault back; | [10 empty] | W | [9 empty] | 1s
20 |  |  |  | wPowerStart Slope | [6 empty] | Power start slope | [10 empty] | W |  |  |  | 1-1000 | [5 empty] | 0.1%
21 |  |  |  | wPowerRest artSlopeEE | [6 empty] | Power restart slope | [10 empty] | W |  |  |  | 1-1000 | [5 empty] | 0.1%
22 |  |  |  | wSelectBaud | [6 empty] | Select | [10 empty] | W |  |  |  | 0-1 | [10 empty] | 0
|  |  |  | rate | [6 empty] | communicationbaudrat
e
0: 9600bps
1:38400bps
23 |  |  |  | Serial NO. 5 | [6 empty] | Serial number 5 | [20 empty] | ASCII
24 |  |  |  | Serial No. 4 | [6 empty] | Serial number 4
25 |  |  |  | Serial No. 3 | [6 empty] | Serial number 3
26 |  |  |  | Serial No. 2 | [6 empty] | Serial number 2
27 |  |  |  | Serial No. 1 | [6 empty] | Serial number 1
28 |  |  |  | Module H | [6 empty] | Inverter Module (high) | [14 empty] | &*5
29 |  |  |  | Module L | [6 empty] | Inverter Module (low) | [14 empty] | &*5
30 |  |  |  | Com Address | [6 empty] | Communicate address | [10 empty] | W |  |  |  | 1-254 | [10 empty] | 1
31 |  |  |  | FlashStart | [6 empty] | Update firmware | [10 empty] | W |  |  |  | 1
32 |  |  |  | Reset User Info | [6 empty] | Reset User Information | [10 empty] | W |  |  |  | 0x0001
33 |  |  |  | Reset to factory | [6 empty] | Reset to factory | [10 empty] | W |  |  |  | 0x0001
34 |  |  |  | Manufacture r Info 8 | [6 empty] | Manufacturer information (high) | [20 empty] | ASCII
35 |  |  |  | Manufacture r Info 7 | [6 empty] | Manufacturer information (middle)
36 |  |  |  | Manufacture r Info 6 | [6 empty] | Manufacturer information (low)
37 |  |  |  | Manufacture r Info 5 | [6 empty] | Manufacturer information (high)
38 |  |  |  | Manufacture r Info 4 | [6 empty] | Manufacturer information (middle)
39 |  |  |  | Manufacture r Info3 | [6 empty] | Manufacturer information (low)
40 |  |  |  | Manufacture r Info 2 | [6 empty] | Manufacturer information (low)
41 |  |  |  | Manufacture r Info 1 | [6 empty] | Manufacturer information (high)
42 |  |  |  | bParallelAnti BackflowHos tNoRespons eFlag | [6 empty] | Parallel Anti-Backflow Host NoResponse Flag | [10 empty] | W |  |  |  | 0 ： Response OK 1 ： NoRespo nse | [11 empty] | Parallel Anti-Backflow Host NoResponse Flag
43 |  |  |  | DTC | [6 empty] | Device Type Code | [14 empty] | &*6
44 |  |  |  | TP | [6 empty] | Input tracker num and output phase num | [14 empty] | Eg:0x020 3 is two MPPT and 3ph output
45 |  |  |  | Sys Year | [6 empty] | System time-year | [10 empty] | W |  |  |  | Year offset is 0 | [11 empty] | Local time
46 |  |  |  | Sys Month | [6 empty] | System time- Month | [10 empty] | W
47 |  |  |  | Sys Day | [6 empty] | System time- Day | [10 empty] | W
48 |  |  |  | Sys Hour | [6 empty] | System time- Hour | [10 empty] | W
49 |  |  |  | Sys Min | [6 empty] | System time- Min | [10 empty] | W
50 |  |  |  | Sys Sec | [6 empty] | System time- Second | [10 empty] | W
51 |  |  |  | Sys Weekly | [6 empty] | System Weekly | [10 empty] | W |  |  |  | 0-6
52 |  |  |  | Vac low | [6 empty] | Grid voltage low limit protect | [10 empty] | W | [9 empty] | 0.1V
53 |  |  |  | Vac high | [6 empty] | Grid voltage high limit protect | [10 empty] | W | [9 empty] | 0.1V
54 |  |  |  | Fac low | [6 empty] | Grid frequency low limit protect | [10 empty] | W | [9 empty] | 0.01 Hz
55 |  |  |  | Fac high | [6 empty] | Grid high frequencylimit protect | [10 empty] | W | [9 empty] | 0.01 Hz
56 |  |  |  | Vac low 2 | [6 empty] | Grid voltage low limit protect 2 | [10 empty] | W | [9 empty] | 0.1V
57 |  |  |  | Vac high 2 | [6 empty] | Grid voltage high limit protect 2 | [10 empty] | W | [9 empty] | 0.1V
58 |  |  |  | Fac low 2 | [6 empty] | Grid frequency low limit protect 2 | [10 empty] | W | [9 empty] | 0.01 Hz
59 |  |  |  | Fac high 2 | [6 empty] | Grid high frequency limit protect 2 | [10 empty] | W | [9 empty] | 0.01 Hz
60 |  |  |  | Vac low 3 | [6 empty] | Grid voltage low limit protect 3 | [10 empty] | W | [9 empty] | 0.1V
61 |  |  |  | Vac high 3 | [6 empty] | Grid voltage high limit protect 3 | [10 empty] | W | [9 empty] | 0.1V
62 |  |  |  | Fac low 3 | [6 empty] | Grid frequency low limit protect 3 | [10 empty] | W | [9 empty] | 0.01Hz
63 |  |  |  | Fac high 3 | [6 empty] | Grid frequency high limit protect 3 | [10 empty] | W | [9 empty] | 0.01Hz
64 |  |  |  | Vac low C | [6 empty] | Grid low voltage limit connect to Grid | [10 empty] | W | [9 empty] | 0.1V
65 |  |  |  | Vac high C | [6 empty] | Grid high voltage limit connect to Grid | [10 empty] | W | [9 empty] | 0.1V
66 |  |  |  | Fac low C | [6 empty] | Grid low frequency limit connect to Grid | [10 empty] | W | [9 empty] | 0.01 Hz
67 |  |  |  | Fac high C | [6 empty] | Grid high frequency limit connect to Grid | [10 empty] | W | [9 empty] | 0.01 Hz
68 |  |  |  | Vac low1 time | [6 empty] | Grid voltage low limit protect time 1 | [10 empty] | W | [9 empty] | Cycle
69 |  |  |  | Vac high1 time | [6 empty] | Grid voltage high limit protect time 1 | [10 empty] | W | [9 empty] | Cycle
70 |  |  |  | Vac low2 time | [6 empty] | Grid voltage low limit protect time 2 | [10 empty] | W | [9 empty] | Cycle
71 |  |  |  | Vac high2 | [6 empty] | Grid voltage high limit | [10 empty] | W | [9 empty] | Cycle
|  |  |  | time | [6 empty] | protect time 2
72 |  |  |  | Fac low1 time | [6 empty] | Grid frequency low limit protect time 1 | [10 empty] | W | [9 empty] | Cycle
73 |  |  |  | Fac high1 time | [6 empty] | Grid frequency high limit protect time 1 | [10 empty] | W | [9 empty] | Cycle
74 |  |  |  | Fac low2 time | [6 empty] | Grid frequency low limit protect time 2 | [10 empty] | W | [9 empty] | Cycle
75 |  |  |  | Fac high2 time | [6 empty] | Grid frequency high limit protect time 2 | [10 empty] | W | [9 empty] | Cycle
76 |  |  |  | Vac low3 time | [6 empty] | Grid voltage low limit protect time 3 | [10 empty] | W | [9 empty] | Cycle
77 |  |  |  | Vac high3 time | [6 empty] | Grid voltage high limit protect time 3 | [10 empty] | W | [9 empty] | Cycle
78 |  |  |  | Fac low3 time | [6 empty] | Grid frequency low limit protect time 3 | [10 empty] | W | [9 empty] | Cycle
79 |  |  |  | Fac high3 time | [6 empty] | Grid frequency high limit protect time 3 | [10 empty] | W | [9 empty] | Cycle
80 |  |  |  | U10min | [6 empty] | Volt protection for 10 min | [10 empty] | W | [9 empty] | 0.1V |  |  |  |  | 1.1Vn
81 |  |  |  | PV Voltage High Fault | [6 empty] | PV Voltage High Fault | [10 empty] | W | [9 empty] | 0.1V
82 |  |  |  | FW Build No. 5 | [6 empty] | FW Build version | [20 empty] | ASCII
83 |  |  |  | FW Build No. 4 | [6 empty] | FW Build version | [20 empty] | ASCII
84 |  |  |  | FW Build No. 3 | [6 empty] | DSP1 FW Build No. | [20 empty] | ASCII
85 |  |  |  | FW Build No. 2 | [6 empty] | DSP2 FW Build No. | [20 empty] | ASCII
86 |  |  |  | FW Build No. 1 | [6 empty] | M3 FW Build No. | [20 empty] | ASCII
87 |  |  |  | FW Build No. 0 | [6 empty] | CPLD FW Build No. | [20 empty] | ASCII
88 |  |  |  | ModbusVers ion | [6 empty] | Modbus Version | [14 empty] | Eg：207 is V2.07 | [5 empty] | Int(16 bits)
89 |  |  |  | PFModel | [6 empty] | Set PF function Model 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power | [10 empty] | W
5: OverExcited(Capa) Reactive Power 6：Q(v)model
90 |  |  |  | GPRS IP Flag | [6 empty] | read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed | [10 empty] | W |  |  |  | about GPRS IP SET
91 |  |  |  | FreqDerateS tart | [6 empty] | Frequency derating start point | [10 empty] | W | [9 empty] | 0.01H Z
92 |  |  |  | FLrate | [6 empty] | Frequency – load limit rate | [10 empty] | W |  |  |  | 0-100 | [5 empty] | 10tim es
93 |  |  |  | V1S | [6 empty] | CEI021 V1S Q(v) | [10 empty] | W |  |  |  | V1S<V2S | [5 empty] | 0.1V
94 |  |  |  | V2S | [6 empty] | CEI021 V2S Q(v) | [10 empty] | W | [9 empty] | 0.1V
95 |  |  |  | V1L | [6 empty] | CEI021 V1L Q(v) | [10 empty] | W |  |  |  | V1L<V1S | [5 empty] | 0.1V
96 |  |  |  | V2L | [6 empty] | CEI021 V2L Q(v) | [10 empty] | W |  |  |  | V2L<V1L | [5 empty] | 0.1V
97 |  |  |  | Qlockinpow er | [6 empty] | Q(v) lock in active power of CEI021 | [10 empty] | W |  |  |  | 0-100 | [5 empty] | Percen t
98 |  |  |  | QlockOutpo wer | [6 empty] | Q(v) lock Out active power of CEI021 | [10 empty] | W |  |  |  | 0-100 | [5 empty] | Percen t
99 |  |  |  | LIGridV | [6 empty] | Lock in gird volt of CEI021 PF line | [10 empty] | W |  |  |  | nVn | [5 empty] | 0.1V
100 |  |  |  | LOGridV | [6 empty] | Lock out gird volt of CEI021 PF line | [10 empty] | W |  |  |  | nVn | [5 empty] | 0.1V
101 |  |  |  | PFAdj1 | [6 empty] | PF adjust value 1 | [14 empty] | 4096 is 1
102 |  |  |  | PFAdj2 | [6 empty] | PF adjust value 2 | [14 empty] | 4096 is 1
103 |  |  |  | PFAdj3 | [6 empty] | PF adjust value 3 | [14 empty] | 4096 is 1
104 |  |  |  | PFAdj4 | [6 empty] | PF adjust value 4 | [14 empty] | 4096 is 1
105 |  |  |  | PFAdj5 | [6 empty] | PF adjust value 5 | [14 empty] | 4096 is 1
106 |  |  |  | PFAdj6 | [6 empty] | PF adjust value 6 | [14 empty] | 4096 is 1
107 |  |  |  | QVRPDelayTi meEE | [6 empty] | QV Reactive Power delaytime | [10 empty] | W |  |  |  | 0-30 | [5 empty] | 1S |  |  |  |  | 3S
108 |  |  |  | OverFDeratD elayTimeEE | [6 empty] | Overfrequency derati ngdelaytime | [10 empty] | W |  |  |  | 0-20 | [5 empty] | 50ms |  |  |  |  | 0
109 |  |  |  | QpercentMa x | [6 empty] | Qmax for Q(V) curve | [10 empty] | W |  |  |  | 0-1000 | [5 empty] | 0.1%
110 |  |  |  | PFLineP1_LP | [6 empty] | PF limit line point 1 load percent | [10 empty] | W |  |  |  | 0-255 | [5 empty] | percen t | [5 empty] | 255 means no this point
111 |  |  |  | PFLineP1_PF | [6 empty] | PF limit line point 1 power factor | [10 empty] | W |  |  |  | 0-20000
112 |  |  |  | PFLineP2_LP | [6 empty] | PF limit line point 2 load percent | [10 empty] | W |  |  |  | 0-255 | [5 empty] | percen t | [5 empty] | 255 means no this point
113 |  |  |  | PFLineP2_PF | [6 empty] | PF limit line point 2power factor | [10 empty] | W |  |  |  | 0-20000
114 |  |  |  | PFLineP3_LP | [6 empty] | PF limit line point 3 load percent | [10 empty] | W |  |  |  | 0-255 | [5 empty] | percen t | [5 empty] | 255 means no this point
115 |  |  |  | PFLineP3_PF | [6 empty] | PF limit line point 3 power factor | [10 empty] | W |  |  |  | 0-20000
116 |  |  |  | PFLineP4_LP | [6 empty] | PF limit line point 4 load percent | [10 empty] | W |  |  |  | 0-255 | [5 empty] | percen t | [5 empty] | 255 means no this point
117 |  |  |  | PFLineP4_PF | [6 empty] | PF limit line point 4 power factor | [10 empty] | W |  |  |  | 0-20000
118 |  |  |  | Module 4 | [6 empty] | Inverter Module (4) | [14 empty] | &*11 | [11 empty] | SxxBxx
119 |  |  |  | Module 3 | [6 empty] | Inverter Module (3) | [14 empty] | &*11 | [11 empty] | DxxTxx
120 |  |  |  | Module 2 | [6 empty] | Inverter Module (2) | [14 empty] | &*11 | [11 empty] | PxxUxx
121 |  |  |  | Module 1 | [6 empty] | Inverter Module (1) | [14 empty] | &*11 | [11 empty] | Mxxxx Power
122 |  |  |  | uwLocalAnti BackflowEna ble | [6 empty] | Local Anti Backflow Enable | [10 empty] | R/W |  |  |  | 1/0 0：disable Not zero： enable | [11 empty] | Local Anti-backflow enable， 0: Disable exportLimit; 1: Enable meter1 exportLimit;(default) 2: Enable meter2 exportLimit; 3: Enable CT exportLimit;
123 |  |  |  | wLocalAntiB ackflowMete rPowerLimit EE | [6 empty] | wLocalAntiBackflowMe terPowerLimitEE | [10 empty] | R/W |  |  |  | -1000~+1 000 | [5 empty] | 0.1% | [5 empty] | Local Anti-backflow power limit percentage
124 |  |  |  | TrakerModel | [6 empty] | 2 Traker Model | [10 empty] | W |  |  |  | 0,1,2 | [5 empty] | 0:Inde pende nt 1:DC Source 2:Paral lel
Second group
125 |  |  |  | INV Type-1 | [6 empty] | Inverter type-1 | [10 empty] | R | [9 empty] | ASCII | [5 empty] | Reserved
126 |  |  |  | INV Type-2 | [6 empty] | Inverter type-2 | [10 empty] | R | [9 empty] | ASCII
127 |  |  |  | INV Type-3 | [6 empty] | Inverter type-3 | [10 empty] | R | [9 empty] | ASCII
128 |  |  |  | INV Type-4 | [6 empty] | Inverter type-4 | [10 empty] | R | [9 empty] | ASCII
129 |  |  |  | INV Type-5 | [6 empty] | Inverter type-5 | [10 empty] | R | [9 empty] | ASCII
130 |  |  |  | INV Type-6 | [6 empty] | Inverter type-06 | [10 empty] | R | [9 empty] | ASCII
131 |  |  |  | INV Type-7 | [6 empty] | Inverter type-7 | [10 empty] | R | [9 empty] | ASCII
132 |  |  |  | INV Type-8 | [6 empty] | Inverter type-8 | [10 empty] | R | [9 empty] | ASCII
133 |  |  |  | BLVersion1 | [6 empty] | Boot loader version1 | [10 empty] | R | [15 empty] | Reserved
134 |  |  |  | BLVersion2 | [6 empty] | Boot loader version2 | [10 empty] | R | [15 empty] | Reserved
135 |  |  |  | BLVersion3 | [6 empty] | Boot loader version3 | [10 empty] | R | [15 empty] | Reserved
136 |  |  |  | BLVersion4 | [6 empty] | Boot loader version4 | [10 empty] | R | [15 empty] | Reserved
…… | [37 empty] | Reserved
200 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserved
201 |  |  |  | PID Working Model | [6 empty] | PID Working Model | [10 empty] | W |  |  |  | 0:Automa tic 1:Continu al 2: Overnight
202 |  |  |  | PID On/Off Ctrl | [6 empty] | PID On/Off Control | [10 empty] | W |  |  |  | 0:On 1:Off
203 |  |  |  | PID Volt Option | [6 empty] | PID Output Voltage Option | [10 empty] | W |  |  |  | 300~1000 | [5 empty] | V
…… | [37 empty] | Reserved
209 |  |  |  | Serial NO New. 15 | [6 empty] | 新序列号 15 | [20 empty] | ASCII
210 |  |  |  | Serial NO. New 14 | [6 empty] | 新序列号 14 | [20 empty] | ASCII
211 |  |  |  | Serial NO. New 13 | [6 empty] | 新序列号 13 | [20 empty] | ASCII
212 |  |  |  | Serial NO. New 12 | [6 empty] | 新序列号 12 | [20 empty] | ASCII
213 |  |  |  | Serial NO. New 11 | [6 empty] | 新序列号 11 | [20 empty] | ASCII
214 |  |  |  | Serial NO. New 10 | [6 empty] | 新序列号 10 | [20 empty] | ASCII
215 |  |  |  | Serial NO. New 9 | [6 empty] | 新序列号 9 | [20 empty] | ASCII
216 |  |  |  | Serial NO. New 8 | [6 empty] | 新序列号 8 | [20 empty] | ASCII
217 |  |  |  | Serial NO. New 7 | [6 empty] | 新序列号 7 | [20 empty] | ASCII
218 |  |  |  | Serial NO. New 6 | [6 empty] | 新序列号 6 | [20 empty] | ASCII
219 |  |  |  | Serial NO. New 5 | [6 empty] | 新序列号 5 | [20 empty] | ASCII
220 |  |  |  | Serial NO. New 4 | [6 empty] | 新序列号 4 | [20 empty] | ASCII
221 |  |  |  | Serial NO. New 3 | [6 empty] | 新序列号 3 | [20 empty] | ASCII
222 |  |  |  | Serial NO New. 2 | [6 empty] | 新序列号 2 | [20 empty] | ASCII
223 |  |  |  | Serial NO New. 1 | [6 empty] | 新序列号 1 | [20 empty] | ASCII
…… | [37 empty] | Reserved
230~249 for growatt debug setting
230 |  |  |  | IslandDisabl e | [6 empty] | Island Disable or not. 1:disable 0:Enable | [10 empty] | W |  |  |  | 0,1 | [10 empty] | 0
231 |  |  |  | FanCheck | [6 empty] | Start Fan Check | [10 empty] | W |  |  |  | 1
232 |  |  |  | EnableNLine | [6 empty] | Enable N Line of grid | [10 empty] | W |  |  |  | 1 | [10 empty] | 0
233 |  |  |  | wCheckHard ware | [6 empty] | wCheckHardware Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarni ng Bit9:EEWriteWarning ……
234 |  |  |  | wCheckHard ware2 | [33 empty] | reserved
235 |  |  |  | ubNToGNDD etect | [6 empty] | Dis/enable N to GND detect function | [10 empty] | W |  |  |  | 1:enable 0:disable | [10 empty] | 1
236 |  |  |  | NonStdVacE nable | [6 empty] | Enable/Disable Nonstandard Grid voltage range | [10 empty] | W |  |  |  | 0-1; | [10 empty] | 0 | 0:Disable; 1:Enable;
237 |  |  |  | uwEnableSp ecSet | [6 empty] | Disablse/enable appointed spec setting | [10 empty] | W |  |  |  | 1:enable 0:disable | [5 empty] | Binary |  |  |  |  | 0x000 0 | Bit 0: Hungary
238 |  |  |  | Fast MPPT enable | [6 empty] | About Fast mppt | [14 empty] | 0,1,2 | [10 empty] | 0 | Reserved
239 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [10 empty] | / | Reserved
240 |  |  |  | Check Step | [17 empty] | W
241 |  |  |  | INV-Lng | [6 empty] | Inverter Longitude | [10 empty] | W | [15 empty] | Longitude
242 |  |  |  | INV-Lat | [6 empty] | Inverter Latitude | [10 empty] | W | [15 empty] | Latitude
…… | [37 empty] | Reserved
249 | [37 empty] | Reserved
250 |  |  |  | Curve analysis | [6 empty] | Enable a curve analysis of a road | [10 empty] | W |  |  |  | 0~1 | [5 empty] | 0
251 |  |  |  | Faultrecorde rWave1 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1001~199 9 | [5 empty] | 1001
252 |  |  |  | Faultrecorde rWave2 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1001~199 9 | [5 empty] | 1002
253 |  |  |  | Faultrecorde | [6 empty] | Preset Record | [10 empty] | W |  |  |  | 1001~199 | [5 empty] | 1003
|  |  |  | rWave3 | [6 empty] | Waveform Number | [14 empty] | 9
254 |  |  |  | Faultrecorde rWave4 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1001~199 9 | [5 empty] | 1004
255 |  |  |  | Faultrecorde rWave5 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~999 | [5 empty] | 1
256 |  |  |  | Faultrecorde rWave6 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~999 | [5 empty] | 2
257 |  |  |  | Faultrecorde rWave7 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~999 | [5 empty] | 3
258 |  |  |  | Faultrecorde rWave8 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~999 | [5 empty] | 4
259 |  |  |  | FaultRecord erEnable | [6 empty] | FaultRecorderEnable | [10 empty] | W |  |  |  | 1~100 | [5 empty] | 0
260 |  |  |  | recorderWav e1 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~1999 | [5 empty] | 1
261 |  |  |  | recorderWav e2 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~1999 | [5 empty] | 2
262 |  |  |  | recorderWav e3 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~1999 | [5 empty] | 3
263 |  |  |  | recorderWav e4 | [6 empty] | Preset Record Waveform Number | [10 empty] | W |  |  |  | 1~1999 | [5 empty] | 4
264 |  |  |  | WaveRecord erEnable | [6 empty] | Real-time waveform recording | [10 empty] | W |  |  |  | 0~1 | [5 empty] | 0
265 |  |  |  | Harmonic Check Enable | [6 empty] | Harmonic Check Enable | [10 empty] | W |  |  |  | 0~1 | [5 empty] | 0
266 |  |  |  | Impedance Enable | [6 empty] | Impedance Enable | [10 empty] | W |  |  |  | 0~1 | [5 empty] | 0
267 |  |  |  | 067 Debug 1 _H | [6 empty] | 067 Debug 1 _H
268 |  |  |  | 067 Debug1_L | [6 empty] | 067 Debug1_L
269 |  |  |  | 067 Debug2_H | [6 empty] | 067 Debug2_H
270 |  |  |  | 067 Debug2_L | [6 empty] | 067 Debug2_L
271 |  |  |  | 067 Debug3_H | [6 empty] | 067 Debug3_H
272 |  |  |  | 067 Debug3_L | [6 empty] | 067 Debug3_L
273 |  |  |  | 67 | [6 empty] | 067 Debug4_H
Debug4_H
274 |  |  |  | 067 Debug4_L | [6 empty] | 067 Debug4_L
275 |  |  |  | 067 Debug5_H | [6 empty] | 067 Debug5_H
276 |  |  |  | 067 Debug5_L | [6 empty] | 067 Debug5_L
277 |  |  |  | 067 Debug6_H | [6 empty] | 067 Debug6_H
278 |  |  |  | 067 Debug6_L | [6 empty] | 067 Debug6_L
279 |  |  |  | 067 Debug7_H | [6 empty] | 067 Debug7_H
280 |  |  |  | 067 Debug7_L | [6 empty] | 067 Debug7_L
281 |  |  |  | 067 Debug8_H | [6 empty] | 067 Debug8_H
282 |  |  |  | 067 Debug8_L | [6 empty] | 067 Debug8_L
283 |  |  |  | 075 Debug 1 _H | [6 empty] | 075 Debug 1 _H
284 |  |  |  | 075 Debug1_L | [6 empty] | 075 Debug1_L
285 |  |  |  | 075 Debug2_H | [6 empty] | 075 Debug2_H
286 |  |  |  | 075 Debug2_L | [6 empty] | 075 Debug2_L
287 |  |  |  | 075 Debug3_H | [6 empty] | 075 Debug3_H
288 |  |  |  | 075 Debug3_L | [6 empty] | 075 Debug3_L
289 |  |  |  | 075 Debug4_H | [6 empty] | 075 Debug4_H
290 |  |  |  | 075 Debug4_L | [6 empty] | 075 Debug4_L
291 |  |  |  | 075 Debug5_H | [6 empty] | 075 Debug5_H
292 |  |  |  | 075 Debug5_L | [6 empty] | 075 Debug5_L
293 |  |  |  | 075 Debug6_H | [6 empty] | 075 Debug6_H
294 |  |  |  | 75 | [6 empty] | 075 Debug6_L
Debug6_L
295 |  |  |  | 075 Debug7_H | [6 empty] | 075 Debug7_H
296 |  |  |  | 075 Debug7_L | [6 empty] | 075 Debug7_L
297 |  |  |  | 075 Debug8_H | [6 empty] | 075 Debug8_H
298 |  |  |  | 075 Debug8_L | [6 empty] | 075 Debug8_L
299 |  |  |  | bActiveOverl oadEnable | [6 empty] | ActiveOverloadEnable
300 |  |  |  | bSvgApfMod e | [6 empty] | SvgApfMode | [14 empty] | Low 4bit： 0:SVG/AP F, 1:APF/SV G, 2:SVG, 3:APF High 4bit: 0:one day mode, 1:Night node,
301 |  |  |  | bBdewLvrtKF actor | [6 empty] | BDEW LVRT KFactor | [14 empty] | 0-7
302 |  |  |  | bBdewZeroC urrentMode En | [6 empty] | BDEW ZeroCurrentMode Enable | [14 empty] | 0-1
303 |  |  |  | bSVGAPFEqu alRatio | [6 empty] | SVG/APFEqualRatio | [14 empty] | 0-32
304 |  |  |  | uwAntiBackf lowFailPowe rLimitEE | [6 empty] | Anti-Backflow Failed PowerRate | [10 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | Anti-Backflow failure default setting power percentage
305 |  |  |  | Qloadspeed | [6 empty] | Q load speed | [10 empty] | R/W |  |  |  | 0-100 | [5 empty] | 1% | [5 empty] | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, directly loaded to the setting value
306 |  |  |  | bParallelAnti BackflowEna ble | [6 empty] | Parallel Anti-Backflow enable | [10 empty] | R/W |  |  |  | 0-1 | [11 empty] | Parallel Anti-Backflow enable 1:Enable 0:Disable
307 |  |  |  | uwAntiBackf | [6 empty] | Anti-Backflow | [10 empty] | R/W |  |  |  | 1-5000 | [5 empty] | 1s | [5 empty] | Anti-backflow failure response
|  |  |  | lowFailureRe sponseTime | [6 empty] | FailureResponseTime | [26 empty] | time
308 |  |  |  | uwParallelAn tiBackflowPo werLimitEE | [6 empty] | Parallel Anti Backflo Power Limit | [9 empty] | R/W w |  |  |  |  | 0-1000 |  |  |  |  | 0.1% | [6 empty] | Parallel Anti Backflow Power Limit
309 |  |  |  | bISOCheckC md | [6 empty] | ISO Check Cmd | [9 empty] | R/W |  |  |  |  | 0-1 |  |  |  |  | 1 | [6 empty] | ISO Check Cmd
310 |  |  |  | bGRPRSStat us | [6 empty] | GPRS status 1 ： Module does no work 2：No SIM 3：No network 4：TCP is connecting t the server 5 ： TCP connectio succeeded | [9 empty] | R/W t o n |  |  |  |  | 0-255 |  |  |  |  | 1 | [6 empty] | GPRS status
Pending part
360 |  |  |  | 232T485Ena | [6 empty] | 232T485Enable | [12 empty] | W |  | 0:
|  |  |  | ble | [21 empty] | Disable;
1: Enable
361 |  |  |  | Decrease | [6 empty] | Decrease output watt | [12 empty] | W
Power H
362 |  |  |  | Decrease | [6 empty] | Decrease output watt | [12 empty] | W | [7 empty] | 0.1W
Power L
363 |  |  |  | Increase | [6 empty] | Increase output watt | [12 empty] | W
Power H
364 |  |  |  | Increase | [6 empty] | Increase output watt | [12 empty] | W | [7 empty] | 0.1W
Power L
365 |  |  |  | Factory | [6 empty] | The ODM Info code
366 |  |  |  | Vac start by | [6 empty] | Vac start adjust by pf | [12 empty] | W | [7 empty] | 0.1V
pf
367 |  |  |  | PF of vac | [6 empty] | Max pf of adjust Vac | [12 empty] | W | [12 empty] | 10000
|  |  |  | limi |  | t
368 |  |  |  | LCMDTest | [6 empty] | Local command test | [9 empty] | W |  |  |  |  | 1 to test
369 |  |  |  | ReactiveRate | [6 empty] | Reactive Rate in LVFRT | [12 empty] | W |  | 0-100 | [10 empty] | 2
370 |  |  |  | LVFRT_LV1 | [6 empty] | LVFRT low fault value | [9 empty] | 1 |  |  | W | [6 empty] | 0.1V
371 |  |  |  | LVFRT_LT1 | [6 empty] | LVFRT low fault time 1 | [12 empty] | W | [6 empty] | 1ms
372 |  |  |  | LVFRT_LV2 | [6 empty] | LVFRT low fault value | [9 empty] | 2 |  |  | W | [6 empty] | 0.1V
373 |  |  |  | LVFRT_LT2 | [6 empty] | LVFRT low fault time 2 | [12 empty] | W | [6 empty] | 1ms
374 |  |  |  | LVFRT_LV3 | [6 empty] | LVFRT low fault value | [9 empty] | 3 |  |  | W | [6 empty] | 0.1V
375 |  |  |  | LVFRT_LT3 | [6 empty] | LVFRT low fault time 3 | [12 empty] | W | [6 empty] | 1ms
376 |  |  |  | LVFRT_LV4 | [6 empty] | LVFRT low fault value | [9 empty] | 4 |  |  | W | [6 empty] | 0.1V
377 |  |  | LVFRT_LT4 | [7 empty] | LVFRT low fault time 4 | [10 empty] | W | [9 empty] | 1ms
378 |  |  | LVFRT_HV1 | [7 empty] | LVFRT high fault value 1 | [10 empty] | W | [9 empty] | 0.1V
379 |  |  | LVFRT_HT1 | [7 empty] | LVFRT high fault time 1 | [10 empty] | W | [9 empty] | 1ms
380 |  |  | wLoadDerat eStartVolt | [7 empty] | Load derate start ac voltage | [14 empty] | 1.05Vn~1 .2Vn | [5 empty] | 0.1V
381 |  |  | SpecPasswor dType | [7 empty] | Unlock or set Specpassword | [10 empty] | W |  |  |  | 0:unlock , auto lock in 5 minute; 1:change pw (should unlock first)， 2：lock, &*7 | [8 empty] | 2
382 |  |  | SpecPasswor d3 | [7 empty] | SpecPassword3 | [10 empty] | W |  |  |  | For the spec setting change | [5 empty] | ASCII |  |  | XX
383 |  |  | SpecPasswor d2 | [7 empty] | SpecPassword2 | [10 empty] | W |  |  |  | .. | [5 empty] | ASCII |  |  | XX
384 |  |  | SpecPasswor d1 | [7 empty] | SpecPassword1 | [10 empty] | W |  |  |  | .. | [5 empty] | ASCII |  |  | XX
385 |  |  | DCIshift | [7 empty] | DCI offset | [14 empty] | Center is 30000 | [8 empty] | Reserved
386 |  |  | DCIAdj | [7 empty] | DCI adjust | [14 empty] | Center is 2000 | [8 empty] | Reserved
387 |  |  | IniEEPROM | [7 empty] | IniEEPROM | [10 empty] | W |  |  |  | 0xFF | [8 empty] | Reserved
388 |  |  | Balance 1 | [7 empty] | Phaseflag¦ErrorCode | [10 empty] | W | [12 empty] | Reserved
389 |  |  | Balance 2 | [7 empty] | Power H | [10 empty] | W | [12 empty] | Reserved
390 |  |  | Balance 3 | [7 empty] | Power L | [10 empty] | W | [12 empty] | Reserved
391 |  |  | bHighACVDe rateSlope | [7 empty] | High ac voltage load derating slope | [10 empty] | W |  |  |  | 20 | [5 empty] | 0-100
392 |  |  | BlaneceMod el | [7 empty] | BlaneceModel | [10 empty] | W |  |  |  | 1-3
393 |  |  | BalencePhas e | [7 empty] | BalencePhase | [10 empty] | W |  |  |  | 1-3
394 |  |  | DCIshift2 | [7 empty] | DCI offset 2 | [10 empty] | W |  |  |  | Center is 30000 | [8 empty] | Reserved
395 |  |  | DCIshift3 | [7 empty] | DCI offset 3 | [10 empty] | W |  |  |  | Center is 30000 | [8 empty] | Reserved
396 |  |  | EnergyLimitE nable | [7 empty] | Output Energy Limit Enable | [10 empty] | R |  |  |  | 1 is enable | [11 empty] | Reserved
397 |  |  | EnergyRemai n H | [7 empty] | Output Energy Limit value High | [10 empty] | W |  |  |  | 0.1kWh | [11 empty] | Reserved
398 |  |  | EnergyRemai n L | [7 empty] | Output Energy Limit value low | [10 empty] | W |  |  |  | 0.1kWh | [11 empty] | Reserved
399 |  |  | TrakerModel | [7 empty] | 2 Traker Model PV model check | [10 empty] | W |  |  |  | 0,1,2 | [11 empty] | SPH
400 |  |  | PMcheck | [7 empty] | Growatt Resaved | [10 empty] | W | [15 empty] | Reserved
401 |  |  | INVWorkMo de | [7 empty] | INV work mode set | [10 empty] | W |  |  |  | 0:default 1:CV Mode 2:CC Mode 3:CP Mode | [8 empty] | 0
402 |  |  | PV1VoltSet | [7 empty] | pv1 voltage set when CV Mode was chosed | [10 empty] | W |  |  |  | StartPVV olt-HighP VVolt
403 |  |  | PV2VoltSet | [7 empty] | Pv2 voltage set when CV Mode was chosed | [10 empty] | W |  |  |  | StartPVV olt-HighP VVolt
404 |  |  | BT1CurrRefS et | [7 empty] | BT1 current set when CC Mode was chosed | [10 empty] | W |  |  |  | 0-MaxBT Current
405 |  |  | BT2CurrRefS et | [7 empty] | BT2current set when CC Mode was chosed | [10 empty] | W |  |  |  | 0-MaxBT Current
406 |  |  | WattACVRec overDelayTi me | [7 empty] | Delay time for power recovering when ac voltage getting normal | [10 empty] | W |  |  |  | 3-90S
407 |  |  | TxDataInterv al | [7 empty] | TxDataInterval | [10 empty] | W |  |  |  | 1~600 | [5 empty] | 0.1 mins |  |  | 50 |  |  | 5mins
408 |  |  | ChkCode NO.1 | [7 empty] | Datalogger Check Code 1 | [10 empty] | R | [9 empty] | ASCII
409 |  |  | ChkCode NO.2 | [7 empty] | Datalogger Check Code 2 | [10 empty] | R | [9 empty] | ASCII
500 |  |  | ChkCode NO.3 | [7 empty] | Datalogger Check Code 3 | [10 empty] | R | [9 empty] | ASCII
501 |  |  | bISLDShiftDe ltaEE | [7 empty] | Growatt Resaved | [10 empty] | W | [15 empty] | Reserved
502 |  |  | bLowPointer | [7 empty] | Growatt Resaved | [10 empty] | W | [15 empty] | Reserved
505 |  |  | GPRSIP Addr | [7 empty] | GPRSIP Addr No.1 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
506 |  |  | GPRSIP Addr | [7 empty] | GPRSIP Addr No.2 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
507 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.3 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
508 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.4 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
509 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.5 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
510 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.6 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
511 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.7 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
512 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.8 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
513 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.9 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
514 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.10 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
515 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.11 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
516 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.12 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
517 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.13 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
518 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.14 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
519 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.15 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
520 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.16 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
521 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.17 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
522 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.18 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
523 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.19 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
524 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.20 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
525 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.21 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
526 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.22 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
527 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.23 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
528 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.24 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
529 |  |  |  | GPRSIP Addr | [6 empty] | GPRSIP Addr No.25 | [10 empty] | W |  |  |  | 0~65536 | [5 empty] | ASCII
Six group for Storage Power
Register NO. |  |  |  | Variable Name | [6 empty] | Description | [10 empty] | Write or not |  |  |  | Value | [5 empty] | Unit |  |  |  |  | Initial value | Note
1000 |  |  |  | Float charge current limit | [6 empty] | When charge current battery need is lower than this value, enter into float charge | [10 empty] | W | [9 empty] | 0.1A |  |  |  |  | 600 | CC current
1001 |  |  |  | PF CMD memory state | [6 empty] | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | [10 empty] | W |  |  |  | 0or1, | [10 empty] | 0 | Means these settings will be acting or not when next power on(02 repeat)
1002 |  |  |  | VbatStartF orDischarg e | [6 empty] | LV Vbat | [10 empty] | R/W | [9 empty] | 0.1V | [5 empty] | Lead-acid battery LV voltage
1003 |  |  |  | VbatlowWa rnClr | [6 empty] | LoadPercent(only lead-Acid): | [10 empty] | W | [9 empty] | 0.1V | [5 empty] | Clear battery low voltage error voltage point
45.5V <20% 48.0V 20%~50% 49.0V >50
1004 |  |  |  | Vbatstopfo rdischarge | [6 empty] | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V <20% 44.8V 20%~50% 44.2V >50% | [10 empty] | W | [9 empty] | 0.01V
1005 |  |  |  | Vbat stop for charge | [6 empty] | Should stop charge when higher than this voltage | [10 empty] | W | [9 empty] | 0.01V |  |  |  |  | 5800
1006 |  |  |  | Vbat start for discharge | [6 empty] | Should not discharge when lower than this voltage | [10 empty] | W | [9 empty] | 0.01V |  |  |  |  | 4800
1007 |  |  |  | Vbat constant charge | [6 empty] | can charge when lower than this voltage | [10 empty] | W | [9 empty] | 0.01V |  |  |  |  | 5800 | CV voltage（acid）
1008 |  |  |  | EESysInfo.S ysSetEn | [6 empty] | Bit0：Resved; Bit1：Resved; Bit2：Resved; Bit3：Resved; Bit4：Resved; Bit5：bDischargeEn； Bit6：ForceDischrEn； Bit7：ChargeEn； Bit8：bForceChrEn； Bit9：bBackUpEn； Bit10：bInvLimitLoadE； Bit11：bSpLimitLoadEn； Bit12：bACChargeEn； Bit13：bPVLoadLimitEn; Bit14,15:UnUsed; | [10 empty] | W | [15 empty] | System Enable
1009 |  |  |  | Battemp lower limit d | [6 empty] | Battery temperature lower limit for discharge | [10 empty] | W |  |  |  | 0-200:0-2 0℃ 1000-140 | [5 empty] | 0.1℃ |  |  |  |  | 1170
0：-40-0℃
1010 |  |  |  | Bat temp upper limit d | [6 empty] | Battery temperature upper limit for discharge | [10 empty] | W |  |  |  | 200-1000 | [5 empty] | 0.1℃ |  |  |  |  | 420
1011 |  |  |  | Bat temp lower limit c | [6 empty] | Battery temperature lower limit for charge | [10 empty] | W |  |  |  | 0-200:0-2 0℃ 1000-140 0：-40-0℃ | [5 empty] | 0.1℃ |  |  |  |  | 30 | Lower temperature limit
1012 |  |  |  | Bat temp upper limit c | [6 empty] | Battery temperature upper limit for charge | [10 empty] | W |  |  |  | 200-1000 | [5 empty] | 0.1℃ |  |  |  |  | 370 | Upper temperature limit
1013 |  |  |  | uwUnderFr eDischarge DelyTime | [6 empty] | Under Fre Delay Time | [10 empty] | s |  |  |  | 0-20 | [5 empty] | 50ms | [5 empty] | Under Fre Delay Time
1014 |  |  |  | BatMdlSeri alNum | [6 empty] | Battery serial number | [10 empty] | W |  |  |  | 00:00 | [11 empty] | SPH4-11K used
1015 |  |  |  | BatMdlPara llNum | [6 empty] | Battery parallel section | [10 empty] | W |  |  |  | 00:00 | [11 empty] | SPH4-11K used
1016 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1017 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1018 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1019 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1020 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1021 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1022 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1023 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1024 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1025 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1026 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1027 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1028 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1029 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1030 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1031 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1032 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1033 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1034 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1035 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1036 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1037 |  |  |  | bCTMode | [6 empty] | Use the CTMode to Choose RFCT \ Cable CT\METER | [10 empty] | W |  |  |  | 2:METER 1:cWirele ssCT 0:cWiredC T | [10 empty] | 0
1038 |  |  |  | CTAdjust | [6 empty] | CTAdjust enable | [10 empty] | W |  |  |  | 0:disable 1:enable | [10 empty] | 0
1039 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1040 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1041 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1042 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / | [5 empty] | Reserve
1043 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1044 |  |  |  | Priority | [6 empty] | ForceChrEn/ForceDischr En Load first/bat first /grid first | [10 empty] | R |  |  |  | 0.Load(de fault)/1.B attery/2.G rid | [11 empty] | bForceChrEn/disbForceDischrE n/dis
1045 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1046 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1047 |  |  |  | AgingTestSt ep Cmd | [6 empty] | Command for aging test | [14 empty] | 0: default 1: charge 2: discharge | [11 empty] | Cmd for aging test
1048 |  |  |  | BatteryTyp e | [6 empty] | Battery type choose of buck-boost input | [14 empty] | 0:Lithium 1:Lead-aci d 2:other | [10 empty] | 0 | Battery type
1049 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / | [5 empty] | Reserve
1050 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
1051 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / | [5 empty] | Reserve
1052 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / | [5 empty] | Reserve
1053 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / | [5 empty] | Reserve
1054 |  |  |  | / | [6 empty] | / | [10 empty] | / |  |  |  | / | [5 empty] | / |  |  |  |  | / | Reserve
Ups information
1060 |  |  |  | BuckUpsFunE n | [8 empty] | Ups function enable or disable | [16 empty] | 0:disable 1:enable
1061 |  |  |  | BuckUPSVoltS et | [8 empty] | UPS output voltage | [16 empty] | 0:230 1:208 2:240 | [7 empty] | 230V
1062 |  |  |  | UPSFreqSet | [8 empty] | UPS output frequency | [16 empty] | 0:50Hz 1:60Hz | [7 empty] | 50Hz
... |  |  |  | / | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / |  |  |  | reverse
Priority set
1070 |  |  |  | GridFirstDisch argePowerRat e | [8 empty] | Discharge Power Rate when Grid First | [12 empty] | W |  |  |  | 0-100 |  |  |  |  | 1% |  |  | Discharge Power Rate when Grid First
1071 |  |  |  | GridFirstStopS OC | [8 empty] | Stop Discharge soc when Grid First | [12 empty] | W |  |  |  | 0-100 |  |  |  |  | 1% |  |  | Stop Discharge soc when Grid First
1072… 1079 |  |  |  | / | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / | [5 empty] | reverse
1080 |  |  |  | Grid First Start Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1081 |  |  |  | Grid First Stop Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1082 |  |  |  | Grid First Stop Switch 1 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Grid First enable
1083 |  |  |  | Grid First Start Time 2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1084 |  |  |  | Grid First Stop Time 2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1085 |  |  |  | Grid First Stop Switch 2 | [8 empty] | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 | [16 empty] | 0 or 1 | [7 empty] | Grid First enable | [5 empty] | ForceDischarge; LCD_SET_FORCE_T RUE_2
1086 |  |  |  | Grid First Start Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1087 |  |  |  | Grid First Stop Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1088 |  |  |  | Grid First Stop Switch 3 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Grid First enable
1089 |  |  |  | / | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / | [5 empty] | reserve
1090 |  |  |  | BatFirstPower Rate | [8 empty] | Charge Power Rate when Bat First | [12 empty] | W |  |  |  | 0-100 |  |  |  |  | 1% |  |  | Charge Power Rate when Bat First
1091 |  |  |  | wBatFirst stop SOC | [8 empty] | Stop Charge soc when Bat First | [12 empty] | W |  |  |  | 0-100 |  |  |  |  | 1% |  |  | Stop Charge soc when Bat First
1092 |  |  |  | AC charge Switch | [8 empty] | When Bat First Enable:1 Disable:0 | [16 empty] | Enable:1 Disable:0 | [7 empty] | AC 充电使能位
1093… 1099
1100 |  |  |  | Bat First Start Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1101 |  |  |  | Bat First Stop Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1102 |  |  |  | BatFirst on/off Switch 1 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Bat First Enable1
1103 |  |  |  | Bat First Start Time 2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1104 |  |  |  | Bat First Stop Time 2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1105 |  |  |  | BatFirston/off Switch 2 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Bat First Enable2
1106 |  |  |  | Bat First Start Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1107 |  |  |  | Bat First Stop Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59
1108 |  |  |  | BatFirston/off Switch 3 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Bat First Enable3
1109 |  |  |  | / | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / | [5 empty] | reserve
1110 |  |  |  | Load First Start Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1111 |  |  |  | Load First Stop Time 1 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1112 |  |  |  | Load First Switch 1 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Load First Enable | [5 empty] | SPA/ reserve
1113 |  |  |  | Load First Start Time2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1114 |  |  |  | Load First Stop Time 2 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1115 |  |  |  | Load First Switch 2 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Load First Enable | [5 empty] | SPA/ reserve
1116 |  |  |  | Load First Start Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1117 |  |  |  | Load First Stop Time 3 | [8 empty] | High eight bit：hour Low eight bit：minute | [16 empty] | 0-23 0-59 | [13 empty] | SPA/ reserve
1118 |  |  |  | Load First Switch 3 | [8 empty] | Enable :1 Disable:0 | [16 empty] | 0 or 1 | [7 empty] | Load First Enable | [5 empty] | SPA/ reserve
1119 |  |  |  | / | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / | [5 empty] | reserve
……… |  |  |  | 1120~1124 | [8 empty] | / | [12 empty] | / |  |  |  | / |  |  |  |  | / |  |  | / | [5 empty] | reserve
Use for TL-X and TL-XH
3000 |  |  |  | ExportLimitFa iledPowerRat e | [8 empty] | The power rate when exportLimit failed | [12 empty] | R/W | [8 empty] | 0.1% | [8 empty] | The power rate when exportLimit failed
3001 |  |  |  | Serial NO New. 15 | [8 empty] | Serial number New 15 | [12 empty] | R/W | [8 empty] | ASCII | [8 empty] | 新机型使用以下寄存器记录序列号； 表示方式与原来一样：一个寄存器保存两个字符，新序列号为 30 个字符。
3002 |  |  |  | Serial NO New. 14 | [8 empty] | Serial number New 14 | [12 empty] | R/W | [8 empty] | ASCII
3003 |  |  |  | Serial NO New. 13 | [8 empty] | Serial number New 13 | [12 empty] | R/W | [8 empty] | ASCII
3004 |  |  |  | Serial NO New. 12 | [8 empty] | Serial number New 12 | [12 empty] | R/W | [8 empty] | ASCII
3005 |  |  |  | Serial NO New. 11 | [8 empty] | Serial number New 11 | [12 empty] | R/W | [8 empty] | ASCII
3006 |  |  |  | Serial NO New. 10 | [8 empty] | Serial number New 10 | [12 empty] | R/W | [8 empty] | ASCII
3007 |  |  |  | Serial NO New. 9 | [8 empty] | Serial number New 9 | [12 empty] | R/W | [8 empty] | ASCII
3008 |  |  |  | Serial NO New. 8 | [8 empty] | Serial number New 8 | [12 empty] | R/W | [8 empty] | ASCII
3009 |  |  |  | Serial NO New. 7 | [8 empty] | Serial number New 7 | [12 empty] | R/W | [8 empty] | ASCII
3010 |  |  |  | Serial NO New. 6 | [8 empty] | Serial number New 6 | [12 empty] | R/W | [8 empty] | ASCII
3011 |  |  |  | Serial NO New. 5 | [8 empty] | Serial number New 5 | [12 empty] | R/W | [8 empty] | ASCII
3012 |  |  |  | Serial NO New. 4 | [8 empty] | Serial number New 4 | [12 empty] | R/W | [8 empty] | ASCII
3013 |  |  |  | Serial NO New. 3 | [8 empty] | Serial number New 3 | [12 empty] | R/W | [8 empty] | ASCII
3014 |  |  |  | Serial NO New. 2 | [8 empty] | Serial number New 2 | [12 empty] | R/W | [8 empty] | ASCII
3015 |  |  |  | Serial NO New. 1 | [8 empty] | Serial number New 1 | [12 empty] | R/W | [8 empty] | ASCII
3016 |  |  |  | DryContactFu ncEn | [8 empty] | DryContact function enable | [12 empty] | R/W |  |  |  | 0:Disable 1: Enable | [13 empty] | DryContact function enable
3017 |  |  |  | DryContactOn Rate | [8 empty] | The power rate of drycontact turn on | [12 empty] | R/W |  |  |  | 0~1000 |  |  |  |  | 0.1% | [8 empty] | The power rate of drycontact turn on
3018 |  |  |  | Reserved
3019 |  |  |  | Reserved
3020 |  |  |  | Reserved
3021 |  |  |  | Reserved
3022 |  |  |  | Reserved
3023 |  |  |  | Reserved
3024 |  |  |  | Float charge current limit | [8 empty] | When charge current battery need is lower than this value, enter into float charge | [12 empty] | R/W | [8 empty] | 0.1A |  |  | 600 | [5 empty] | CC current
3025 |  |  |  | VbatWarning | [8 empty] | "Battery-low" warning setup voltage | [12 empty] | R/W | [8 empty] | 0.1V |  |  | 4800 | [5 empty] | Lead acid battery LV voltage
3026 |  |  |  | VbatlowWarn Clr | [8 empty] | "Battery-low" warning clear voltage | [12 empty] | R/W | [8 empty] | 0.1V | [8 empty] | Clear battery low voltage error voltage point LoadPercent(only lead-Acid): 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%);
3027 |  |  |  | Vbatstopfordi scharge | [8 empty] | Battery cut off voltage | [12 empty] | R/W | [8 empty] | 0.1V | [8 empty] | Should stop discharge when lower than this voltage(only lead-Acid):
46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%);
3028 |  |  |  | Vbat stop for charge | [8 empty] | Battery over charge voltage | [12 empty] | R/W | [8 empty] | 0.01V |  |  | 5800 | [5 empty] | Should stop charge when higher than this voltage
3029 |  |  |  | Vbat start for discharge | [8 empty] | Battery start discharge voltage | [12 empty] | R/W | [8 empty] | 0.01V |  |  | 4800 | [5 empty] | Should not discharge when lower than this voltage
3030 |  |  |  | Vbat constant charge | [8 empty] | Battery constant charge voltage | [12 empty] | R/W | [8 empty] | 0.01V |  |  | 5800 | [5 empty] | CV voltage（acid） can charge when lower than this voltage
3031 |  |  |  | Battemp lower limit d | [8 empty] | Battery temperature lower limit for discharge | [12 empty] | R/W | [8 empty] | 0.1℃ |  |  | 1170 | [5 empty] | 0-200:0-20℃ 1000-1400： -40-0℃
3032 |  |  |  | Bat temp upper limit d | [8 empty] | Battery temperature upper limit for discharge | [12 empty] | R/W | [8 empty] | 0.1℃ |  |  | 420
3033 |  |  |  | Bat temp lower limit c | [8 empty] | Battery temperature lower limit for charge | [12 empty] | R/W | [8 empty] | 0.1℃ |  |  | 30 | [5 empty] | Battery temperature lower limit 0-200:0-20℃ 1000-1400： -40-0℃
3034 |  |  |  | Bat temp upper limit c | [8 empty] | Battery temperature upper limit for charge | [12 empty] | R/W | [8 empty] | 0.1℃ |  |  | 370 | [5 empty] | Battery temperature upper limit
3035 |  |  |  | uwUnderFreD ischargeDelyT ime | [8 empty] | Under Fre Delay Time | [12 empty] | R/W | [8 empty] | 50ms | [8 empty] | Under Fre Delay Time
3036 |  |  |  | GridFirstDisch argePowerRat e | [8 empty] | Discharge Power Rate when Grid First
3037 |  |  |  | GridFirstStopS OC | [8 empty] | Stop Discharge soc when Grid First
3038 |  |  |  | Grid First Start Time 1 | [8 empty] | Grid First Start Time 1 | [30 empty] | High eight bit : hour,0-23
Low eight bit : minute,0-59
3039 |  |  |  | Grid First Stop Time 1 | [8 empty] | Grid First Stop Time 1 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3040 |  |  |  | Grid First Stop Switch 1 | [8 empty] | Grid first time-1 enable | [30 empty] | Enable :1 Disable:0
3041 |  |  |  | Grid First Start Time 2 | [8 empty] | Grid First Start Time 2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3042 |  |  |  | Grid First Stop Time 2 | [8 empty] | Grid First Stop Time 2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3043 |  |  |  | Grid First Stop Switch 2 | [8 empty] | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 | [30 empty] | ForceDischarge; LCD_SET_FORCE_T RUE_2
3044 |  |  |  | Grid First Start Time 3 | [8 empty] | Grid First Start Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3045 |  |  |  | Grid First Stop Time 3 | [8 empty] | Grid First Stop Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3046 |  |  |  | Grid First Stop Switch 3 | [8 empty] | Grid first time-3 enable | [30 empty] | Enable :1 Disable:0
3047 |  |  |  | BatFirstPower Rate | [8 empty] | Charge Power Rate when Bat First
3048 |  |  |  | wBatFirst stop SOC | [8 empty] | Stop Charge soc when Bat First
3049 |  |  |  | AC charge Switch | [8 empty] | When Bat First Enable :1 Disable:0 | [30 empty] | Enable :1 Disable:0
3050 |  |  |  | Bat First Start Time 1 | [8 empty] | Bat First Start Time 1 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3051 |  |  |  | Bat First Stop Time 1 | [8 empty] | Bat First Stop Time 1 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3052 |  |  |  | BatFirst on/off Switch 1 | [8 empty] | Battery first time-1 enable | [30 empty] | Enable :1 Disable:0
3053 |  |  |  | Bat First Start Time 2 | [8 empty] | Bat First Start Time 2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3054 |  |  |  | Bat First Stop Time 2 | [8 empty] | Bat First Stop Time 2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3055 |  |  |  | BatFirston/off Switch 2 | [8 empty] | Battery first time-2 enable | [30 empty] | Enable :1 Disable:0
3056 |  |  |  | Bat First Start Time 3 | [8 empty] | Bat First Start Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3057 |  |  |  | Bat First Stop Time 3 | [8 empty] | Bat First Stop Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3058 |  |  |  | BatFirston/off Switch 3 | [8 empty] | Battery first time-3 enable | [30 empty] | Enable :1 Disable:0
3059 |  |  |  | Load First Start Time 1 | [8 empty] | Load First Start Time 1 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3060 |  |  |  | Load First Stop Time 1 | [8 empty] | Load First Stop Time 1 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3061 |  |  |  | Load First Switch 1 | [8 empty] | Enable :1 Disable:0 | [30 empty] | Enable :1 Disable:0
3062 |  |  |  | Load First Start Time2 | [8 empty] | Load First Start Time2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3063 |  |  |  | Load First Stop Time 2 | [8 empty] | Load First Stop Time 2 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3064 |  |  |  | Load First Switch 2 | [8 empty] | Enable :1 Disable:0 | [30 empty] | Enable :1 Disable:0
3065 |  |  |  | Load First Start Time 3 | [8 empty] | Load First Start Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3066 |  |  |  | Load First Stop Time 3 | [8 empty] | Load First Stop Time 3 | [30 empty] | High eight bit : hour,0-23 Low eight bit : minute,0-59
3067 |  |  |  | Load First Switch 3 | [8 empty] | Enable :1 Disable:0 | [30 empty] | Enable :1 Disable:0
3068 |  |  |  | bCTMode | [8 empty] | Use the CTMode to Choose RFCT \ Cable CT\METER | [12 empty] | R/W | [17 empty] | CTMode 0: CT selfAdjust; 1:cWiredCT 2:cWirelessCT 3:METER
3069 |  |  |  | Priority | [8 empty] | ForceChrEn/ForceDischrEn Load first/bat first /grid first | [12 empty] | R/W | [17 empty] | ForceChrEn/Force DischrEn Load first/bat first /grid first 0.Load(default)/1. Battery/2.Grid
3070 |  |  |  | BatteryType | [8 empty] | Battery type choose of buck-boost input | [12 empty] | R/W | [17 empty] | Battery type 0:Lithium 1:Lead-acid 2:other
3071 |  |  |  | BatMdlSeria/ ParalNum | [8 empty] | BatMdlSeria/ParalNum | [12 empty] | R/W | [17 empty] | BatMdlSeria/Paral Num; SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits indicate the number of parallel
sections;
3072 |  |  |  | Reserved
3073 |  |  |  | Reserved
3074 |  |  |  | Reserved
3075 |  |  |  | Reserved
3076 |  |  |  | Reserved
3077 |  |  |  | Reserved
3078 |  |  |  | Reserved
3079 |  |  |  | UpsFunEn | [8 empty] | Ups function enable or disable | [12 empty] | R/W | [11 empty] | 0 | [5 empty] | 0:disable 1:enable
3080 |  |  |  | UPSVoltSet | [8 empty] | UPS output voltage | [12 empty] | R/W | [11 empty] | 0 | [5 empty] | 0:230V 1:208V 2:240V
3081 |  |  |  | UPSFreqSet | [8 empty] | UPS output frequency | [12 empty] | R/W | [11 empty] | 0 | [5 empty] | 0:50Hz 1:60Hz
3082 |  |  |  | Reserved
3083 |  |  |  | Reserved
3084 |  |  |  | Reserved
3085 |  |  |  | Com Address | [8 empty] | Communication addr | [12 empty] | R/W | [11 empty] | 1 | [5 empty] | 1 : Communication addr=1 1 ~ 254 : Communication addr=1~254
3086 |  |  |  | BaudRate | [8 empty] | Communication BaudRate | [12 empty] | R/W | [11 empty] | 0 | [5 empty] | 0: 9600 bps 1: 38400 bps
3087 |  |  |  | Serial NO. 5 | [8 empty] | Serial Number 5 | [12 empty] | R/W | [8 empty] | ASCII
3088 |  |  |  | Serial No. 4 | [8 empty] | Serial Number 4 | [12 empty] | R/W | [8 empty] | ASCII
3089 |  |  |  | Serial No. 3 | [8 empty] | Serial Number 3 | [12 empty] | R/W | [8 empty] | ASCII
3090 |  |  |  | Serial No. 2 | [8 empty] | Serial Number 2 | [12 empty] | R/W | [8 empty] | ASCII
3091 |  |  |  | Serial No. 1 | [8 empty] | Serial Number 1 | [12 empty] | R/W | [8 empty] | ASCII
3092 |  |  |  | Model H | [8 empty] | Model H | [12 empty] | R/W
3093 |  |  |  | Model L | [8 empty] | Model L | [12 empty] | R/W
3094 |  |  |  | Pdischr max H | [8 empty] | Max Discharge Power | [12 empty] | R | [8 empty] | 0.1W
3095 |  |  |  | Pdischr max L
3096 |  |  |  | Pchr max H | [8 empty] | Max Charge Power | [12 empty] | R | [8 empty] | 0.1W
3097 |  |  |  | Pchr max L
3098 |  |  |  | DTC | [8 empty] | DTC | [12 empty] | R
3099 |  |  |  | FW Code1 | [8 empty] | FW Code1 | [12 empty] | R | [8 empty] | ASCII
3100 |  |  |  | FW Code2 | [8 empty] | FW Code2 | [12 empty] | R | [8 empty] | ASCII
3101 |  |  |  |  | Processor1 FW Vision | [7 empty] | Processor1 FW Vision | [12 empty] | R | [9 empty] | ASCII
3102 |  |  |  |  | Reset User Info | [7 empty] | Reset User Info | [12 empty] | W
3103 |  |  |  |  | Reset to factory | [7 empty] | Reset to factory | [12 empty] | W
3104 ~ 3124 |  |  |  |  | Reserved
说明：1.Load First 设置 SPA 使用；
4.2 Input Reg (Some of inputRegisters can be wrote by Manufacturer, write address offset is 0x1000, start at 0x1000.can notbe wrote by customer.)
NO. |  |  | Variable Name | [11 empty] | Description | [18 empty] | Value | [6 empty] | Unit |  |  |  |  | Note
First group
0 |  |  |  | Inverter Status | [10 empty] | Inverter run state | [18 empty] | 0:waiting, 1:normal, 3:fault
1 |  |  |  | Ppv H | [10 empty] | Input power (high) | [25 empty] | 0.1W
2 |  |  |  | Ppv L | [10 empty] | Input power (low) | [25 empty] | 0.1W
3 |  |  |  | Vpv1 | [10 empty] | PV1 voltage | [25 empty] | 0.1V
4 |  |  |  | PV1Curr | [10 empty] | PV1 input current | [25 empty] | 0.1A
5 |  |  |  | Ppv1 H | [10 empty] | PV1 input power(high) | [25 empty] | 0.1W
6 |  |  |  | Ppv1 L | [10 empty] | PV1 input power(low) | [25 empty] | 0.1W
7 |  |  |  | Vpv2 | [10 empty] | PV2 voltage | [25 empty] | 0.1V
8 |  |  |  | PV2Curr | [10 empty] | PV2 input current | [25 empty] | 0.1A
9 |  |  |  | Ppv2 H | [10 empty] | PV2 input power (high) | [25 empty] | 0.1W
10 |  |  |  | Ppv2 L | [10 empty] | PV2 input power (low) | [25 empty] | 0.1W
11 |  |  |  | Vpv3 | [10 empty] | PV3 voltage | [25 empty] | 0.1V
12 |  |  |  | PV3Curr | [10 empty] | PV3 input current | [25 empty] | 0.1A
13 |  |  |  | Ppv3 H | [10 empty] | PV3 input power (high) | [25 empty] | 0.1W
14 |  |  |  | Ppv3 L | [10 empty] | PV3 input power (low) | [25 empty] | 0.1W
15 |  |  |  | Vpv4 | [10 empty] | PV4 voltage | [25 empty] | 0.1V
16 |  |  |  | PV4Curr | [10 empty] | PV4 input current | [25 empty] | 0.1A
17 |  |  |  | Ppv4 H | [10 empty] | PV4 input power (high) | [25 empty] | 0.1W
18 |  |  |  | Ppv4 L | [10 empty] | PV4 input power (low) | [25 empty] | 0.1W
19 |  |  |  | Vpv5 | [10 empty] | PV5 voltage | [25 empty] | 0.1V
20 |  |  |  | PV5Curr | [10 empty] | PV5 input current | [25 empty] | 0.1A
21 |  |  |  | Ppv5H | [10 empty] | PV5 input power(high) | [25 empty] | 0.1W
22 |  |  |  | Ppv5 L | [10 empty] | PV5 input power(low) | [25 empty] | 0.1W
23 |  |  |  | Vpv6 | [10 empty] | PV6 voltage | [25 empty] | 0.1V
24 |  |  |  | PV6Curr | [10 empty] | PV6 input current | [25 empty] | 0.1A
25 |  |  |  | Ppv6 H | [10 empty] | PV6 input power (high) | [25 empty] | 0.1W
26 |  |  |  | Ppv6 L | [10 empty] | PV6 input power (low) | [25 empty] | 0.1W
27 |  |  |  | Vpv7 | [10 empty] | PV7 voltage | [25 empty] | 0.1V
28 |  |  |  | PV7Curr | [10 empty] | PV7 input current | [25 empty] | 0.1A
29 |  |  |  | Ppv7 H | [10 empty] | PV7 input power (high) | [25 empty] | 0.1W
30 |  |  |  | Ppv7 L | [10 empty] | PV7 input power (low) | [25 empty] | 0.1W
31 |  |  |  | Vpv8 | [10 empty] | PV8 voltage | [25 empty] | 0.1V
32 |  |  |  | PV8Curr | [10 empty] | PV8 input current | [25 empty] | 0.1A
33 |  |  |  | Ppv8 H | [10 empty] | PV8 input power (high) | [25 empty] | 0.1W
34 |  |  |  | Ppv8 L | [10 empty] | PV8 input power (low) | [25 empty] | 0.1W
35 |  |  |  | Pac H | [10 empty] | Output power (high) | [25 empty] | 0.1W
36 |  |  |  | Pac L | [10 empty] | Output power (low) | [25 empty] | 0.1W
37 |  |  |  | Fac | [10 empty] | Grid frequency | [25 empty] | 0.01Hz
38 |  |  |  | Vac1 | [10 empty] | Three/single phase grid voltage | [25 empty] | 0.1V
39 |  |  |  | Iac1 | [10 empty] | Three/single phase grid output current | [25 empty] | 0.1A
40 |  |  |  | Pac1 H | [10 empty] | Three/single phase grid output watt VA (high) | [25 empty] | 0.1VA
41 |  |  |  | Pac1 L | [10 empty] | Three/single phase grid output watt VA(low) | [25 empty] | 0.1VA
42 |  |  |  | Vac2 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
43 |  |  |  | Iac2 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A
44 |  |  |  | Pac2 H | [10 empty] | Three phase grid output power (high) | [25 empty] | 0.1VA
45 |  |  |  | Pac2 L | [10 empty] | Three phase grid output power (low) | [25 empty] | 0.1VA
46 |  |  |  | Vac3 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
47 |  |  |  | Iac3 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A
48 |  |  |  | Pac3 H | [10 empty] | Three phase grid output power (high) | [25 empty] | 0.1VA
49 |  |  |  | Pac3 L | [10 empty] | Three phase grid output power (low) | [25 empty] | 0.1VA
50 |  |  |  | Vac_RS | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
51 |  |  |  | Vac_ST | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
52 |  |  |  | Vac_TR | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
53 |  |  |  | Eactoday H | [10 empty] | Today generate energy (high) | [25 empty] | 0.1kWH
54 |  |  |  | Eac today L | [10 empty] | Today generate energy (low) | [25 empty] | 0.1kWH
55 |  |  |  | Eac total H | [10 empty] | Total generate energy (high) | [25 empty] | 0.1kWH
56 |  |  |  | Eac total L | [10 empty] | Total generate energy (low) | [25 empty] | 0.1kWH
57 |  |  |  | Time total H | [10 empty] | Work time total (high) | [25 empty] | 0.5s
58 |  |  |  | Time total L | [10 empty] | Work time total (low) | [25 empty] | 0.5s
59 |  |  |  | Epv1_today H | [10 empty] | PV1Energy today(high) | [25 empty] | 0.1kWh
60 |  |  |  | Epv1_today L | [10 empty] | PV1Energy today (low) | [25 empty] | 0.1kWh
61 |  |  |  | Epv1_total H | [10 empty] | PV1Energy total(high) | [25 empty] | 0.1kWh
62 |  |  |  | Epv1_total L | [10 empty] | PV1Energy total (low) | [25 empty] | 0.1kWh
63 |  |  |  | Epv2_today H | [10 empty] | PV2Energy today(high) | [25 empty] | 0.1kWh
64 |  |  |  | Epv2_today L | [10 empty] | PV2Energy today (low) | [25 empty] | 0.1kWh
65 |  |  |  | Epv2_total H | [10 empty] | PV2Energy total(high) | [25 empty] | 0.1kWh
66 |  |  |  | Epv2_total L | [10 empty] | PV2Energy total (low) | [25 empty] | 0.1kWh
67 |  |  |  | Epv3_today H | [10 empty] | PV3 Energy today(high) | [25 empty] | 0.1kWh
68 |  |  |  | Epv3_today L | [10 empty] | PV3 Energy today (low) | [25 empty] | 0.1kWh
69 |  |  |  | Epv3_total H | [10 empty] | PV3 Energy total(high) | [25 empty] | 0.1kWh
70 |  |  |  | Epv3_total L | [10 empty] | PV3 Energy total (low) | [25 empty] | 0.1kWh
71 |  |  |  | Epv4_today H | [10 empty] | PV4Energy today(high) | [25 empty] | 0.1kWh
72 |  |  |  | Epv4_today L | [10 empty] | PV4Energy today (low) | [25 empty] | 0.1kWh
73 |  |  |  | Epv4_total H | [10 empty] | PV4Energy total(high) | [25 empty] | 0.1kWh
74 |  |  |  | Epv4_total L | [10 empty] | PV4Energy total (low) | [25 empty] | 0.1kWh
75 |  |  |  | Epv5_today H | [10 empty] | PV5Energy today(high) | [25 empty] | 0.1kWh
76 |  |  |  | Epv5_today L | [10 empty] | PV5Energy today (low) | [25 empty] | 0.1kWh
77 |  |  |  | Epv5_total H | [10 empty] | PV5Energy total(high) | [25 empty] | 0.1kWh
78 |  |  |  | Epv5_total L | [10 empty] | PV5Energy total (low) | [25 empty] | 0.1kWh
79 |  |  |  | Epv6_today H | [10 empty] | PV6Energy today(high) | [25 empty] | 0.1kWh
80 |  |  |  | Epv6_today L | [10 empty] | PV6Energy today (low) | [25 empty] | 0.1kWh
81 |  |  |  | Epv6_total H | [10 empty] | PV6Energy total(high) | [25 empty] | 0.1kWh
82 |  |  |  | Epv6_total L | [10 empty] | PV6Energy total (low) | [25 empty] | 0.1kWh
83 |  |  |  | Epv7_today H | [10 empty] | PV7Energy today(high) | [25 empty] | 0.1kWh
84 |  |  |  | Epv7_today L | [10 empty] | PV7Energy today (low) | [25 empty] | 0.1kWh
85 |  |  |  | Epv7_total H | [10 empty] | PV7 Energy total(high) | [25 empty] | 0.1kWh
86 |  |  |  | Epv7_total L | [10 empty] | PV7Energy total (low) | [25 empty] | 0.1kWh
87 |  |  |  | Epv8_today H | [10 empty] | PV8Energy today(high) | [25 empty] | 0.1kWh
88 |  |  |  | Epv8_today L | [10 empty] | PV8Energy today (low) | [25 empty] | 0.1kWh
89 |  |  |  | Epv8_total H | [10 empty] | PV8Energy total(high) | [25 empty] | 0.1kWh
90 |  |  |  | Epv8_total L | [10 empty] | PV8Energy total (low) | [25 empty] | 0.1kWh
91 |  |  |  | Epv_total H | [10 empty] | PV Energy total(high) | [25 empty] | 0.1kWh
92 |  |  |  | Epv_total L | [10 empty] | PV Energy total (low) | [25 empty] | 0.1kWh
93 |  |  |  | Temp1 | [10 empty] | Inverter temperature | [25 empty] | 0.1C
94 |  |  |  | Temp2 | [10 empty] | The inside IPM in inverter Temperature | [25 empty] | 0.1C
95 |  |  |  | Temp3 | [10 empty] | Boost temperature | [25 empty] | 0.1C
96 |  |  |  | Temp4 | [41 empty] | reserved
97 |  |  |  | uwBatVolt_DSP | [10 empty] | BatVolt_DSP | [25 empty] | 0.1V |  |  |  |  | BatVolt(DSP)
98 |  |  |  | P Bus Voltage | [10 empty] | P Bus inside Voltage | [25 empty] | 0.1V
99 |  |  |  | N Bus Voltage | [10 empty] | N Bus inside Voltage | [25 empty] | 0.1V
100 |  |  |  | IPF | [10 empty] | Inverter output PF now | [18 empty] | 0-20000
101 |  |  |  | RealOPPercent | [10 empty] | Real Output power Percent | [25 empty] | 1%
102 |  |  |  | OPFullwatt H | [10 empty] | Output Maxpower Limited high
103 |  |  |  | OPFullwatt L | [10 empty] | Output Maxpower Limited low | [25 empty] | 0.1W
104 |  |  |  | DeratingMode | [10 empty] | DeratingMode | [18 empty] | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime; | [11 empty] | “*”is Reserved
105 |  |  |  | Fault code | [10 empty] | Inverter fault code | [18 empty] | &*1
106 |  |  |  | Fault Bitcode H | [10 empty] | Inverter fault code high | [18 empty] | &*8
107 |  |  |  | Fault Bitcode L | [10 empty] | Inverter fault code low
108 |  |  |  | RemoteCtrlEn | [10 empty] | / | [18 empty] | 0.Load First 1.BatFirst 2.Grid | [6 empty] | / |  |  |  |  | StoragePow er (SPA)
109 |  |  |  | RemoteCtrlPow er | [10 empty] | / | [25 empty] | / |  |  |  |  | StoragePow er (SPA)
110 |  |  |  | Warning bit H | [10 empty] | Warning bit H | [18 empty] | &*8
111 |  |  |  | Warning bit L | [10 empty] | Warning bit L
112 |  |  |  | bINVWarnCode | [10 empty] | bINVWarnCode | [30 empty] | MAX
|  |  |  | EACharge_Today _H | [10 empty] | ACCharge energy today | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
113 |  |  |  | real Power Percent | [10 empty] | real Power Percent | [18 empty] | 0-100 | [6 empty] | % |  |  |  |  | MAX
|  |  |  | EACharge_Today _L | [10 empty] | ACCharge energy today | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
114 |  |  |  | inv start delay time | [10 empty] | inv start delay time | [30 empty] | MAX
|  |  |  | EACharge_Total _H | [10 empty] | ACCharge energy total | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
115 |  |  |  | bINVAllFaultCod e | [10 empty] | bINVAllFaultCode | [30 empty] | MAX
|  |  |  | EACharge_Total | [10 empty] | ACCharge energy total | [25 empty] | 0.1kwh |  |  |  |  | Storage
|  |  |  | _L | [41 empty] | Power
116 |  |  |  | AC charge Power_H | [10 empty] | Grid power to local load | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
117 |  |  |  | AC charge Power_L | [10 empty] | Grid power to local load | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
118 |  |  |  | Priority | [10 empty] | 0:Load First 1:Battery First 2:Grid First | [30 empty] | Storage Power
119 |  |  |  | Battery Type | [10 empty] | 0：Lead-acid 1：Lithium battery | [30 empty] | Storage Power
120 |  |  |  | AutoProofreadC MD | [10 empty] | Aging mode 自动校准命令 | [30 empty] | Storage Power
… |  |  |  | reserved | [41 empty] | reserved
124 |  |  |  | reserved | [41 empty] | reserved
Second group
125 |  |  |  | PID PV1+ Voltage | [11 empty] | PID PV1PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
126 |  |  |  | PID PV1+ Current | [11 empty] | PID PV1PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
127 |  |  |  | PID PV2+ Voltage | [11 empty] | PID PV2PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
128 |  |  |  | PID PV2+ Current | [11 empty] | PID PV2PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
129 |  |  |  | PID PV3+ Voltage | [11 empty] | PID PV3PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
130 |  |  |  | PID PV3+ Current | [11 empty] | PID PV3PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
131 |  |  |  | PID PV4+ Voltage | [11 empty] | PID PV4PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
132 |  |  |  | PID PV4+ Current | [11 empty] | PID PV4PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
133 |  |  |  | PID PV5+ Voltage | [11 empty] | PID PV5PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
134 |  |  |  | PID PV5+ Current | [11 empty] | PID PV5PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
135 |  |  |  | PID PV6+ Voltage | [11 empty] | PID PV6PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
136 |  |  |  | PID PV6+ Current | [11 empty] | PID PV6PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
137 |  |  |  | PID PV7+ Voltage | [11 empty] | PID PV7PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
138 |  |  |  | PID PV7+ Current | [11 empty] | PID PV7PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
139 |  |  |  | PID PV8+ Voltage | [11 empty] | PID PV8PE Volt | [17 empty] | 0~1000V | [6 empty] | 0.1V
140 |  |  |  | PID PV8+ Current | [11 empty] | PID PV8PE Curr | [17 empty] | -10~10mA | [6 empty] | 0.1mA
141 |  |  |  | PID Status | [11 empty] | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | [17 empty] | 0~3
142 |  |  |  | V _String1 | [11 empty] | PV String1 voltage | [24 empty] | 0.1V
143 |  |  |  | Curr _String1 | [11 empty] | PV String1 current | [17 empty] | -15~15A | [6 empty] | 0.1A
144 |  |  |  | V _String2 | [11 empty] | PV String2 voltage | [24 empty] | 0.1V
145 |  |  |  | Curr _String2 | [11 empty] | PV String2 current | [17 empty] | -15~15A | [6 empty] | 0.1A
146 |  |  |  | V _String3 | [11 empty] | PV String3 voltage | [24 empty] | 0.1V
147 |  |  |  | Curr _String3 | [11 empty] | PV String3 current | [17 empty] | -15~15A | [6 empty] | 0.1A
148 |  |  |  | V _String4 | [11 empty] | PV String4 voltage | [24 empty] | 0.1V
149 |  |  |  | Curr _String4 | [11 empty] | PV String4 current | [17 empty] | -15~15A | [6 empty] | 0.1A
150 |  |  |  | V _String5 | [11 empty] | PV String5 voltage | [24 empty] | 0.1V
151 |  |  |  | Curr _String5 | [11 empty] | PV String5 current | [17 empty] | -15~15A | [6 empty] | 0.1A
152 |  |  |  | V _String6 | [11 empty] | PV String6 voltage | [24 empty] | 0.1V
153 |  |  |  | Curr _String6 | [11 empty] | PV String6 current | [17 empty] | -15~15A | [6 empty] | 0.1A
154 |  |  |  | V _String7 | [11 empty] | PV String7 voltage | [24 empty] | 0.1V
155 |  |  |  | Curr _String7 | [11 empty] | PV String7 current | [17 empty] | -15~15A | [6 empty] | 0.1A
156 |  |  |  | V _String8 | [11 empty] | PV String8 voltage | [24 empty] | 0.1V
157 |  |  |  | Curr _String8 | [11 empty] | PV String8 current | [17 empty] | -15A~15A | [6 empty] | 0.1A
158 |  |  |  | V _String9 | [11 empty] | PV String9 voltage | [24 empty] | 0.1V
159 |  |  |  | Curr _String9 | [11 empty] | PV String9 current | [17 empty] | -15A~15A | [6 empty] | 0.1A
160 |  |  |  | V _String10 | [11 empty] | PV String10 voltage | [24 empty] | 0.1V
161 |  |  |  | Curr _String10 | [11 empty] | PV String10 current | [17 empty] | -15~15A | [6 empty] | 0.1A
162 |  |  |  | V _String11 | [11 empty] | PV String11 voltage | [24 empty] | 0.1V
163 |  |  |  | Curr _String11 | [11 empty] | PV String11 current | [17 empty] | -15~15A | [6 empty] | 0.1A
164 |  |  |  | V _String12 | [11 empty] | PV String12 voltage | [24 empty] | 0.1V
165 |  |  |  | Curr _String12 | [11 empty] | PV String12 current | [17 empty] | -15~15A | [6 empty] | 0.1A
166 |  |  |  | V _String13 | [11 empty] | PV String13 voltage | [24 empty] | 0.1V
167 |  |  |  | Curr _String13 | [11 empty] | PV String13 current | [17 empty] | -15A~15A | [6 empty] | 0.1A
168 |  |  |  | V _String14 | [11 empty] | PV String14 voltage | [24 empty] | 0.1V
169 |  |  |  | Curr _String14 | [11 empty] | PV String14 current | [17 empty] | -15~15A | [6 empty] | 0.1A
170 |  |  |  | V _String15 | [11 empty] | PV String15 voltage | [24 empty] | 0.1V
171 |  |  |  | Curr _String15 | [11 empty] | PV String15 current | [17 empty] | -15~15A | [6 empty] | 0.1A
172 |  |  |  | V _String16 | [11 empty] | PV String16 voltage | [24 empty] | 0.1V
173 |  |  |  | Curr _String16 | [11 empty] | PV String16 current | [17 empty] | -15~15A | [6 empty] | 0.1A
174 |  |  |  | StrUnmatch | [11 empty] | Bit0~15: String1~16 unmatch | [29 empty] | suggestive
175 |  |  |  | StrCurrentUnblan ce | [11 empty] | Bit0~15: String1~16 current unblance | [29 empty] | suggestive
176 |  |  |  | StrDisconnect | [11 empty] | Bit0~15: String1~16 disconnect | [29 empty] | suggestive
177 |  |  |  | PIDFaultCode | [11 empty] | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved
178 |  |  |  | String Prompt | [11 empty] | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance Bit3~15:reserved
179 |  |  |  | PV Warning Value | [11 empty] | PV Warning Value
180 |  |  |  | DSP075 Warning Value | [11 empty] | DSP075 Warning Value
181 |  |  |  | DSP075 Fault Value | [11 empty] | DSP075 Fault Value
182 |  |  |  | DSP067 Debug Data1 | [11 empty] | DSP067 Debug Data1
183 |  |  |  | DSP067 Debug Data2 | [11 empty] | DSP067 Debug Data2
184 |  |  |  | DSP067 Debug Data3 | [11 empty] | DSP067 Debug Data3
185 |  |  |  | DSP067 Debug Data4 | [11 empty] | DSP067 Debug Data4
186 |  |  |  | DSP067 Debug Data5 | [11 empty] | DSP067 Debug Data5
187 |  |  |  | DSP067 Debug Data6 | [11 empty] | DSP067 Debug Data6
188 |  |  |  | DSP067 Debug Data7 | [11 empty] | DSP067 Debug Data7
189 |  |  |  | DSP067 Debug Data8 | [11 empty] | DSP067 Debug Data8
190 |  |  |  | DSP075 Debug Data1 | [11 empty] | DSP075 Debug Data1
191 |  |  |  | DSP075 Debug Data2 | [11 empty] | DSP075 Debug Data2
192 |  |  |  | DSP075 Debug Data3 | [11 empty] | DSP075 Debug Data3
193 |  |  |  | DSP075 Debug Data4 | [11 empty] | DSP075 Debug Data4
194 |  |  |  | DSP075 Debug Data55 | [11 empty] | DSP075 Debug Data5
195 |  |  |  | DSP075 Debug Data6 | [11 empty] | DSP075 Debug Data6
196 |  |  |  | DSP075 Debug Data7 | [11 empty] | DSP075 Debug Data7
197 |  |  |  | DSP075 Debug Data8 | [11 empty] | DSP075 Debug Data8
198 |  |  |  | bUSBAgingTestOk Flag | [11 empty] | USBAgingTestOkFlag | [17 empty] | 0-1
199 |  |  |  | bFlashEraseAging OkFlag | [11 empty] | FlashEraseAgingOkFlag | [17 empty] | 0-1
200 |  |  |  | PVISO | [11 empty] | PVISOValue | [24 empty] | KΩ
201 |  |  |  | R_DCI | [11 empty] | R DCI Curr | [24 empty] | 0.1mA
202 |  |  |  | S_DCI | [11 empty] | S DCI Curr | [24 empty] | 0.1mA
203 |  |  |  | T_DCI | [11 empty] | T DCI Curr | [24 empty] | 0.1mA
204 |  |  |  | PID_Bus | [11 empty] | PIDBusVolt | [24 empty] | 0.1V
205 |  |  |  | GFCI | [11 empty] | GFCI Curr | [24 empty] | mA
206 |  |  |  | SVG/APF Status+SVGAPFEq ualRatio | [11 empty] | SVG/APF Status+SVGAPFEqualRatio | [17 empty] | High 8bit： SVGAPFEqua lRatio Low 8bit： SVG/APF Status 0:None 1:SVG Run 2:APF Run 3:SVG/APF Run
207 |  |  |  | CT_I _R | [11 empty] | R phase load side current for SVG | [24 empty] | 0.1A
208 |  |  |  | CT_I _S | [11 empty] | S phase load side current for SVG | [24 empty] | 0.1A
209 |  |  |  | CT_I _T | [11 empty] | T phase load side current for SVG | [24 empty] | 0.1A
210 |  |  |  | CT_Q _R H | [11 empty] | R phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
211 |  |  |  | CT_Q _R L | [11 empty] | R phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
212 |  |  |  | CT_Q _S H | [11 empty] | S phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
213 |  |  |  | CT_Q _S L | [11 empty] | S phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
214 |  |  |  | CT_Q _T H | [11 empty] | T phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
215 |  |  |  | CT_Q _T L | [11 empty] | T phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
216 |  |  |  | CT HAR_I_R | [11 empty] | R phase load side harmonic | [24 empty] | 0.1A
217 |  |  |  | CT HAR_I_S | [11 empty] | S phase load side harmonic | [24 empty] | 0.1A
218 |  |  |  | CT HAR_I_T | [11 empty] | T phase load side harmonic | [24 empty] | 0.1A
219 |  |  |  | COMP_Q _R H | [11 empty] | R phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
220 |  |  |  | COMP_Q _R L | [11 empty] | R phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
221 |  |  |  | COMP_Q _S H | [11 empty] | S phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
222 |  |  |  | COMP_Q _S L | [11 empty] | S phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
223 |  |  |  | COMP_Q _T H | [11 empty] | T phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
224 |  |  |  | COMP_Q _T L | [11 empty] | T phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
225 |  |  |  | COMP HAR_I_R | [11 empty] | R phase compensate harmonic for SVG | [24 empty] | 0.1A
226 |  |  |  | COMP HAR_I_S | [11 empty] | S phase compensate harmonic for SVG | [24 empty] | 0.1A
227 |  |  |  | COMP HAR_I_T | [11 empty] | T phase compensate harmonic for SVG | [24 empty] | 0.1A
228 |  |  |  | bRS232AgingTest OkFlag | [11 empty] | RS232AgingTestOkFlag | [17 empty] | 0-1
229 |  |  |  | bFanFaultBit | [11 empty] | Bit0：Fan1 Fault Bit Bit1：Fan2 Fault Bit Bit2：Fan3 Fault Bit Bit3：Fan4 Fault Bit Bit4-7：reserved
230 |  |  |  | Sac H | [11 empty] | Output apparent power (high) | [24 empty] | 0.1W
231 |  |  |  | Sac L | [11 empty] | Output apparent power (low) | [24 empty] | 0.1W
… |  |  |  | 232~249 | [41 empty] | reserved
Third group
250 |  |  | Grid Fault record 1 – code | [11 empty] | Grid Fault record 1 – code
251 |  |  | Grid Fault record 1 – year¦ month | [11 empty] | Grid Fault record 1 – year¦ month | [18 empty] | Year offset is 2000
252 |  |  | Grid Fault record 1 – day¦ hour | [11 empty] | Grid Fault record 1 – day¦ hour
253 |  |  | Grid Fault record 1 – min¦ sec | [11 empty] | Grid Fault record 1 – min¦ sec
254 |  |  | Grid Fault record 1-value | [11 empty] | Grid Fault record 1-value | [18 empty] | &*2
255 |  |  | Grid Fault record 2 – code | [11 empty] | Grid Fault record 2 – code
256 |  |  | Grid Fault record 2 – year¦ month | [11 empty] | Grid Fault record 2 – year¦ month | [18 empty] | Year offset is 2000
257 |  |  | Grid Fault record 2 – day¦ hour | [11 empty] | Grid Fault record 2 – day¦ hour
258 |  |  | Grid Fault record 2 – min¦ sec | [11 empty] | Grid Fault record 2 – min¦ sec
259 |  |  | Grid Fault record 2-value | [11 empty] | Grid Fault record 2-value
260 |  |  | Grid Fault record 3 | [11 empty] | Grid Fault record 3 – code
– code
261 |  |  | Grid Fault record 3 – year¦ month | [11 empty] | Grid Fault record 3 – year¦ month | [18 empty] | Year offset is 2000
262 |  |  | Grid Fault record 3 – day¦ hour | [11 empty] | Grid Fault record 3 – day¦ hour
263 |  |  | Grid Fault record 3 – min¦ sec | [11 empty] | Grid Fault record 3 – min¦ sec
264 |  |  | Grid Fault record 3-value | [11 empty] | Grid Fault record 3-value
265 |  |  | Grid Fault record 4 – code | [11 empty] | Grid Fault record 4 – code
266 |  |  | Grid Fault record 4 – year¦ month | [11 empty] | Grid Fault record 4 – year¦ month | [18 empty] | Year offset is 2000
267 |  |  | Grid Fault record 4 – day¦ hour | [11 empty] | Grid Fault record 4 – day¦ hour
268 |  |  | Grid Fault record 4 – min¦ sec | [11 empty] | Grid Fault record 4 – min¦ sec
269 |  |  | Grid Fault record 4-value | [11 empty] | Grid Fault record 4-value
270 |  |  | Grid Fault record 5 – code | [11 empty] | Grid Fault record 5 – code
271 |  |  | Grid Fault record 5 – year¦ month | [11 empty] | Grid Fault record 5 – year¦ month | [18 empty] | Year offset is 2000
272 |  |  | Grid Fault record 5 – day¦ hour | [11 empty] | Grid Fault record 5 – day¦ hour
273 |  |  | Grid Fault record 5 – min¦ sec | [11 empty] | Grid Fault record 5 – min¦ sec
274 |  |  | Grid Fault record 5-value | [11 empty] | Grid Fault record 5-value
275 |  |  | bTestProcess<<8 ¦ bAutoTestStep | [11 empty] | Auto test process or auto test step | [18 empty] | &*3
276 |  |  | wAutoTestResult | [11 empty] | Auto test result | [18 empty] | &*4
277 |  |  | cTestStepStop | [11 empty] | Auto test stop step | [18 empty] | &*4
278 |  |  | Value Limit | [11 empty] | Safety voltage/frequency limit value | [25 empty] | 0.1V
279 |  |  | Time Limit | [11 empty] | Safety time limit value | [25 empty] | 1ms
280 |  |  | Real value | [11 empty] | Real voltage/frequency value | [25 empty] | 0.1V
281 |  |  | Test value | [11 empty] | Auto testing voltage/frequency value | [25 empty] | 0.1V
282 |  |  | Test treat value | [11 empty] | Auto test voltage/frequency treat value | [25 empty] | 0.1V
283 |  |  | Test treat time | [11 empty] | Auto test treat time | [25 empty] | 1ms
284 |  |  | E_hour0 H | [11 empty] | Energy hourly of this day
285 |  |  | E_hour0 L | [11 empty] | Energy hourly of this day
286 |  |  | E_hour1 H | [11 empty] | Energy hourly of this day
287 |  |  | E_hour1 L | [11 empty] | Energy hourly of this day
… |  |  | E_hour | [11 empty] | …
… |  |  | E_hour | [11 empty] | …
330 |  |  | E_hour23 H | [11 empty] | Energy hourly of this day
331 |  |  | E_hour23 L | [11 empty] | Energy hourly of this day
332 |  |  | E_ day0 H | [11 empty] | Energy of latest day
333 |  |  | E_day0 L | [11 empty] | Energy of latest day
334 |  |  | E_ day1 H | [11 empty] | Energy of latest 1st day
335 |  |  | E_ day1 L | [11 empty] | Energy of latest 1st day
… |  |  | E_ day | [11 empty] | …
… |  |  | E_ day | [11 empty] | …
344 |  |  | E_ day 6 H | [11 empty] | Energy of latest 6th day
345 |  |  | E_ day 6L | [11 empty] | Energy of latest 6th day
346 |  |  | E_ month0 H | [11 empty] | Energy of latest month
347 |  |  | E_ month0 L | [11 empty] | Energy of latest month
|  |  | E_ month1 H | [11 empty] | Energy of latest 1st month
|  |  | E_ month1 L | [11 empty] | Energy of latest 1st month
… |  |  | E_ month | [11 empty] | …
… |  |  | E_ month | [11 empty] | …
368 |  |  | E_ month11 H | [11 empty] | Energy of latest 11th month
369 |  |  | E_ month11L | [11 empty] | Energy of latest 11th month
… | [45 empty] | reserved
374 | [45 empty] | reserved
Fouth group
375 |  |  | E_ year0 H | [11 empty] | Energy of latest year
376 |  |  | E_ year 0 L | [11 empty] | Energy of latest year
377 |  |  | E_ year 1 H | [11 empty] | Energy of latest 1st year
378 |  |  | E_ year 1 L | [11 empty] | Energy of latest 1st year
… |  |  | E_ year | [11 empty] | …
… |  |  | E_ year | [11 empty] | …
413 |  |  | E_ year 18 H | [11 empty] | Energy of latest 18th year
414 |  |  | E_ year18 L | [11 empty] | Energy of latest 18th year
…
499 | [45 empty] | reserved
Fifth group and sixth
500 |  |  |  | Inverter Error record 1 – code | [10 empty] | Inverter Error record 1 – code
501 |  |  |  | Inverter Error record 1 – year¦ | [10 empty] | Inverter Error record 1 – year¦ month | [18 empty] | Year offset is 2000
month
502 |  |  |  | Inverter Error record 1 – day¦ hour | [10 empty] | Inverter Error record 1 – day¦ hour
503 |  |  |  | Inverter Error record 1 – min¦ sec | [10 empty] | Inverter Error record 1 – min¦ sec
504 |  |  |  | Inverter Error record 1-value | [10 empty] | Inverter Error record 1-value
505 |  |  |  | Inverter Error record 2 – code | [10 empty] | Inverter Error record 2 – code
506 |  |  |  | Inverter Error record 2 – year¦ month | [10 empty] | Inverter Error record 2 – year¦ month | [18 empty] | Year offset is 2000
507 |  |  |  | Inverter Error record 2 – day¦ hour | [10 empty] | Inverter Error record 2 – day¦ hour
508 |  |  |  | Inverter Error record 2 – min¦ sec | [10 empty] | Inverter Error record 2 – min¦ sec
509 |  |  |  | Inverter Error record 2-value | [10 empty] | Inverter Error record 2-value
510 |  |  |  | Inverter Error record 2 – code | [10 empty] | Inverter Error record 2 – code
… |  |  |  | Inverter Error record…… | [10 empty] | Inverter Error record……
740 |  |  |  | Inverter Error record49 – code | [10 empty] | Inverter Error record 49- code
741 |  |  |  | Inverter Error record49 – year¦ month | [10 empty] | Inverter Error record49 – year¦ month | [18 empty] | Year offset is 2000
742 |  |  |  | Inverter Error record49 – day¦ hour | [10 empty] | Inverter Error record49 – day¦ hour
743 |  |  |  | Inverter Error record49 – min¦ sec | [10 empty] | Inverter Error record49 – min¦ sec
744 |  |  |  | Inverter Error record49-value | [10 empty] | Inverter Error record49-value
745 |  |  |  | Inverter Error record50 – code | [10 empty] | Inverter Error record 50- code
746 |  |  |  | Inverter Error | [10 empty] | Inverter Error record50 – year¦ month | [18 empty] | Year offset is
|  |  |  | record50 – year¦ month | [29 empty] | 2000
747 |  |  |  | Inverter Error record50 – day¦ hour | [10 empty] | Inverter Error record50 – day¦ hour
748 |  |  |  | Inverter Error record50 – min¦ sec | [10 empty] | Inverter Error record50 – min¦ sec
749 |  |  |  | Inverter Error record50-value | [10 empty] | Inverter Error record50-value
Seventh group for debug
750 |  |  |  | ISO fault Value | [10 empty] | ISO Fault value | [25 empty] | 0.1V
751 |  |  |  | GFCI fault Value | [10 empty] | GFCI fault Value | [25 empty] | 1mA
752 |  |  |  | DCI fault Value | [10 empty] | DCI fault Value | [25 empty] | 0.01A
753 |  |  |  | Vpv fault Value | [10 empty] | PV voltage fault value | [25 empty] | 0.1V
754 |  |  |  | Vac fault Value | [10 empty] | AC voltage fault value | [25 empty] | 0.1V
755 |  |  |  | Fac fault Value | [10 empty] | AC frequency fault value | [25 empty] | 0.01 Hz
756 |  |  |  | Temperature fault Value | [10 empty] | Temperature fault value | [25 empty] | 0.1C
757 |  |  |  | WarningValue1 | [10 empty] | Warning Value1 of slave CPU | [18 empty] | &*9
758 |  |  |  | WarningValue2 | [10 empty] | Warning Value2 of slave CPU | [18 empty] | &*9
759 |  |  |  | WarningValue3 | [10 empty] | Warning Value3 of main CPU or STM32 | [18 empty] | &*9
760 |  |  |  | FaultValue | [10 empty] | Inverter fault value | [18 empty] | &*10
...
799
800 |  |  |  | Debug Reserved | [10 empty] | Debug Reserved | [30 empty] | Reserved
……
874 |  |  |  | Debug Reserved | [10 empty] | Debug Reserved | [30 empty] | Reserved
Eighth group for reserved
……
999 |  |  |  | SystemCmd | [10 empty] | M3 to DSP System Cmd | [30 empty] | System cmd
Ninth group for Storage power
1000 |  |  |  | uwSysWorkMode | [12 empty] | System work mode | [14 empty] | 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03：SysFault module 0x04: Flash | [12 empty] | 监控层给客户显示的工作模式为： 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash
[32 empty] | module 0x05 ： PVBATOnline module, 0x06 ： BatOnline module, 0x07 ： PVOfflineMod e module, 0x08 ： BatOfflineMo de module, | [12 empty] | module 0x05¦0x06¦0x07¦0 x08:normal module
1001 |  |  |  | Systemfault word0 | [12 empty] | System fault word0 | [27 empty] | 详见一体机故障 说明
1002 |  |  |  | Systemfault word1 | [12 empty] | System fault word1
1003 |  |  |  | Systemfault word2 | [12 empty] | System fault word2
1004 |  |  |  | Systemfault word3 | [12 empty] | System fault word3
1005 |  |  |  | Systemfault word4 | [12 empty] | System fault word4
1006 |  |  |  | Systemfault word5 | [12 empty] | System fault word5
1007 |  |  |  | Systemfault word6 | [12 empty] | System fault word6
1008 |  |  |  | Systemfault word7 | [12 empty] | System fault word7
1009 |  |  |  | Pdischarge1 H | [12 empty] | Discharge power(high) | [22 empty] | 0.1W
1010 |  |  |  | Pdischarge1 L | [12 empty] | Discharge power (low) | [22 empty] | 0.1W
1011 |  |  |  | Pcharge1 H | [12 empty] | Charge power(high) | [22 empty] | 0.1W
1012 |  |  |  | Pcharge1 L | [12 empty] | Charge power (low) | [22 empty] | 0.1W
1013 |  |  |  | Vbat | [12 empty] | Battery voltage | [22 empty] | 0.1V
1014 |  |  |  | SOC | [12 empty] | State of charge Capacity | [14 empty] | 0-100 | [7 empty] | 1% |  |  |  |  | lith/leadacid
1015 |  |  |  | Pactouser R | [7 empty] | H |  |  |  |  | AC power to user H | [22 empty] | 0.1w
1016 |  |  |  | Pactouser R | [7 empty] | L |  |  |  |  | AC power to user L | [22 empty] | 0.1w
1017 |  |  |  | Pactouser S | [7 empty] | H |  |  |  |  | Pactouser S | [5 empty] | H | [16 empty] | 0.1w
1018 |  |  |  | Pactouser S | [7 empty] | L |  |  |  |  | Pactouser S | [5 empty] | L | [16 empty] | 0.1w
1019 |  |  |  | Pactouser T | [7 empty] | H |  |  |  |  | Pactouser T | [5 empty] | H | [16 empty] | 0.1w
1020 |  |  |  | Pactouser T | [7 empty] | L |  |  |  |  | Pactouser T | [5 empty] | H | [16 empty] | 0.1w
1021 |  |  |  | PactouserTotal H | [12 empty] | AC power to user total H | [22 empty] | 0.1w
1022 |  |  |  | PactouserTotal L | [12 empty] | AC power to user total L | [22 empty] | 0.1w
1023 |  |  |  | Pac to grid R | [7 empty] | H |  |  |  |  | AC power to grid H | [22 empty] | 0.1w |  |  |  |  | Ac output
1024 |  |  |  | Pac to grid R | [7 empty] | L |  |  |  |  | AC power to grid L | [22 empty] | 0.1w
1025 |  |  |  | Pactogrid S | [7 empty] | H | [27 empty] | 0.1w
1026 |  |  |  | Pactogrid S | [7 empty] | L | [27 empty] | 0.1w
1027 |  |  |  | Pactogrid T H | [35 empty] | 0.1w
1028 |  |  |  | Pactogrid T L | [35 empty] | 0.1w
1029 |  |  |  | Pactogrid total H | [12 empty] | AC power to grid total H | [22 empty] | 0.1w
1030 |  |  |  | Pactogrid total L | [12 empty] | AC power to grid total L | [22 empty] | 0.1w
1031 |  |  |  | PLocalLoad R H | [12 empty] | INV power to local load H | [22 empty] | 0.1w
1032 |  |  |  | PLocalLoad R L | [12 empty] | INV power to local load L | [22 empty] | 0.1w
1033 |  |  |  | PLocalLoad S H | [35 empty] | 0.1w
1034 |  |  |  | PLocalLoad S L | [35 empty] | 0.1w
1035 |  |  |  | PLocalLoadT H | [35 empty] | 0.1w
1036 |  |  |  | PLocalLoadT L | [35 empty] | 0.1w
1037 |  |  |  | PLocalLoad total H | [12 empty] | INV power to local load total H | [22 empty] | 0.1w
1038 |  |  |  | PLocalLoad total L | [12 empty] | INV power to local load total L | [22 empty] | 0.1w
1039 |  |  |  | IPM Temperature | [12 empty] | REC Temperature | [22 empty] | 0.1℃ |  |  |  |  | No use
1040 |  |  |  | Battery Temperature | [12 empty] | Battery Temperature | [22 empty] | 0.1℃ |  |  |  |  | Lead acid/lithium battery temp
1041 |  |  |  | SP DSP Status | [12 empty] | SP state | [27 empty] | CHG/DisCHG
1042 |  |  |  | SP Bus Volt | [12 empty] | SP BUS2 Volt | [22 empty] | 0.1V
1043 |  |  |  | / | [12 empty] | / | [14 empty] | / | [7 empty] | / |  |  |  |  | reserved
发电量数据
1044 |  |  | Etouser_today H | [11 empty] | Energy to user today high | [24 empty] | 0.1kWh
1045 |  |  | Etouser_today L | [11 empty] | Energy to user today low | [24 empty] | 0.1kWh
1046 |  |  | Etouser_total H | [11 empty] | Energy to user total high | [24 empty] | 0.1kWh
1047 |  |  | Etouser_ total L | [11 empty] | Energy to user total high | [24 empty] | 0.1kWh
1048 |  |  | Etogrid_today H | [11 empty] | Energy to grid today high | [24 empty] | 0.1kWh
1049 |  |  | Etogrid _today L | [11 empty] | Energy to grid today low | [24 empty] | 0.1kWh
1050 |  |  | Etogrid _total H | [11 empty] | Energy to grid total high | [24 empty] | 0.1kWh
1051 |  |  | Etogrid _ total L | [11 empty] | Energy to grid total high | [24 empty] | 0.1kWh
1052 |  |  | Edischarge1_toda y H | [11 empty] | Discharge energy1 today | [24 empty] | 0.1kWh
1053 |  |  | Edischarge1_toda y L | [11 empty] | Discharge energy1 today | [24 empty] | 0.1kWh
1054 |  |  | Edischarge1_total H | [11 empty] | Total discharge energy1 (high) | [24 empty] | 0.1kWh
1055 |  |  | Edischarge1_total L | [11 empty] | Total discharge energy1 (low) | [24 empty] | 0.1kWh
1056 |  |  | Echarge1_today H | [11 empty] | Charge1 energy today | [24 empty] | 0.1kWh
1057 |  |  | Echarge1_today L | [11 empty] | Charge1 energy today | [24 empty] | 0.1kWh
1058 |  |  | Echarge1_total H | [11 empty] | Charge1 energy total | [24 empty] | 0.1kWh
1059 |  |  | Echarge1_total L | [11 empty] | Charge1 energy total | [24 empty] | 0.1kWh
1060 |  |  | ELocalLoad_Today | [11 empty] | Local load energy today | [24 empty] | 0.1kWh
H
1061 |  |  | ELocalLoad_Today L | [11 empty] | Local load energy today | [23 empty] | 0.1kWh
1062 |  |  | ELocalLoad_Total H | [11 empty] | Local load energy total | [23 empty] | 0.1kWh
1063 |  |  | ELocalLoad_Total L | [11 empty] | Local load energy total | [23 empty] | 0.1kWh
1064 |  |  | dwExportLimitAp parentPower | [11 empty] | ExportLimitApparentPower H | [23 empty] | 0.1kWh | [5 empty] | ApparentPower
1065 |  |  | dwExportLimitAp parentPower | [11 empty] | ExportLimitApparentPower L | [23 empty] | 0.1kWh | [5 empty] | ApparentPower
1066 |  |  | / | [11 empty] | / | [16 empty] | / | [6 empty] | / | [5 empty] | reserved
Ups information (offline)
1067 |  |  | EPS Fac | [11 empty] | UPSfrequency | [16 empty] | 5000/6000 | [6 empty] | 0.01Hz
1068 |  |  | EPS Vac1 | [11 empty] | UPS phase R output voltage | [16 empty] | 2300 | [6 empty] | 0.1V
1069 |  |  | EPS Iac1 | [11 empty] | UPS phase R output current | [23 empty] | 0.1A
1070 |  |  | EPS Pac1 H | [11 empty] | UPS phase R output power (H) | [23 empty] | 0.1VA
1071 |  |  | EPS Pac1 L | [11 empty] | UPS phase R output power (L) | [23 empty] | 0.1VA
1072 |  |  | EPS Vac2 | [11 empty] | UPS phase S output voltage | [23 empty] | 0.1V
1073 |  |  | EPS Iac2 | [11 empty] | UPS phase S output current | [23 empty] | 0.1A | [5 empty] | No use
1074 |  |  | EPS Pac2 H | [11 empty] | UPS phase S output power (H) | [23 empty] | 0.1VA
1075 |  |  | EPS Pac2 L | [11 empty] | UPS phase S output power (L) | [23 empty] | 0.1VA
1076 |  |  | EPS Vac3 | [11 empty] | UPS phase T output voltage | [23 empty] | 0.1V
1077 |  |  | EPS Iac3 | [11 empty] | UPS phase T output current | [23 empty] | 0.1A | [5 empty] | No use
1078 |  |  | EPS Pac3 H | [11 empty] | UPS phase T output power (H) | [23 empty] | 0.1VA
1079 |  |  | EPS Pac3 L | [11 empty] | UPS phase T output power (L) | [23 empty] | 0.1VA
1080 |  |  | Loadpercent | [11 empty] | Load percent of UPS ouput | [16 empty] | 0-100 | [6 empty] | 1%
1081 |  |  | PF | [11 empty] | Power factor | [16 empty] | 0-2 | [6 empty] | 0.1 | [5 empty] | Primary Value+1
BMS 类信息
1082 |  |  |  | BMS_StatusOld | [10 empty] | StatusOld from BMS | [16 empty] | Detail information, refer to document:GrowattxxSxx P ESS Protocol;
1083 |  |  |  | BMS_Status | [10 empty] | Status from BMS | [29 empty] | W/R
1084 |  |  |  | BMS_ErrorOld | [10 empty] | Error info Old from BMS
1085 |  |  |  | BMS_Error | [10 empty] | Errorinfomation from BMS
1086 |  |  |  | BMS_SOC | [10 empty] | SOC from BMS | [29 empty] | R SPH6K
1087 |  |  |  | BMS_BatteryVol t | [10 empty] | Battery voltage from BMS | [29 empty] | R SPH6K
1088 |  |  |  | BMS_BatteryCur r | [10 empty] | Battery current from BMS
1089 |  |  |  | BMS_BatteryTe mp | [10 empty] | Battery temperature from BMS
1090 |  |  |  | BMS_MaxCurr | [10 empty] | Max. charge/discharge current
from BMS (pylon)
1091 |  |  |  | BMS_GaugeRM | [10 empty] | Gauge RM from BMS
1092 |  |  |  | BMS_GaugeFCC | [10 empty] | Gauge FCC from BMS
1093 |  |  |  | BMS_FW
1094 |  |  |  | BMS_DeltaVolt | [10 empty] | Delta V from BMS
1095 |  |  |  | BMS_CycleCnt | [10 empty] | Cycle Count from BMS
1096 |  |  |  | BMS_SOH | [10 empty] | SOH from BMS
1097 |  |  |  | BMS_ConstantV olt | [10 empty] | CV voltage from BMS
1098 |  |  |  | BMS_WarnInfoO ld | [10 empty] | Warning info old from BMS
1099 |  |  |  | BMS_WarnInfo | [10 empty] | Warning info from BMS
1100 |  |  |  | BMS_GaugeICCu rr | [10 empty] | Gauge IC current from BMS
1101 |  |  |  | BMS_MCUVersi on | [10 empty] | MCU Software version from BMS
1102 |  |  |  | BMS_GaugeVers ion | [10 empty] | Gauge Version from BMS
1103 |  |  |  | BMS_wGaugeFR Version_ L | [10 empty] | Gauge FR Version L16 from BMS
1104 |  |  |  | BMS_wGaugeFR Version_H | [10 empty] | Gauge FR Version H16 from BMS
1105 |  |  |  | BMS_BMSInfo | [10 empty] | BMSInformation from BMS
1106 |  |  |  | BMS_PackInfo | [10 empty] | Pack Information from BMS
1107 |  |  |  | BMS_UsingCap | [10 empty] | Using Cap from BMS
1108 |  |  |  | BMS_ Cell1_Volt | [10 empty] | Cell1_Voltage from BMS
1109 |  |  |  | BMS_ Cell2_Volt | [10 empty] | Cell_Voltage from BMS
…
1123 |  |  |  | BMS_ Cell16_Volt | [10 empty] | Cell16_Voltage from BMS
1124 |  |  |  | AC Charge Energy Today H | [10 empty] | AC Charge Energy today | [16 empty] | kwh | [12 empty] | Energy today
Ninth group reserved for storage power
1125 |  |  |  | ACCharge Energy TodayL | [10 empty] | AC Charge Energy today | [16 empty] | kwh
1126 |  |  |  | AC Charge Energy Total H | [40 empty] | Energy total
1127 |  |  |  | ACCharge Energy Total L
1128 |  |  |  | AC Charge Power H | [10 empty] | AC Charge Power | [16 empty] | W
1129 |  |  |  | AC Charge Power L | [10 empty] | AC Charge Power | [16 empty] | w
1130 |  |  |  | 70% INV Power adjust | [10 empty] | uwGridPower_70_AdjEE_SP | [16 empty] | W
1131 |  |  |  | Extra AC Power to grid_H | [10 empty] | Extra inverte AC Power to grid High | [16 empty] | For SPA connect inverter | [12 empty] | SPA used
1132 |  |  |  | Extra AC Power to grid_L | [10 empty] | Extrainverte AC Power to grid Low | [29 empty] | SPA used
1133 |  |  |  | Eextra_today H | [10 empty] | Extra inverter PowerTOUser_Extra today (high) | [16 empty] | R | [6 empty] | 0.1kWh | [5 empty] | SPA | used
1134 |  |  |  | Eextra_today L | [10 empty] | Extra inverter PowerTOUser_Extra today (low) | [16 empty] | R | [6 empty] | 0.1kWh | [5 empty] | SPA | used
1135 |  |  |  | Eextra_total H | [10 empty] | Extra inverter PowerTOUser_Extra total(high) | [23 empty] | 0.1kWh | [5 empty] | SPA | used
1136 |  |  |  | Eextra_total L | [10 empty] | Extra inverter PowerTOUser_Extra total(low) | [23 empty] | 0.1kWh | [5 empty] | SPA | used
1137 |  |  |  | Esystem_today H | [10 empty] | System electric energy today H | [23 empty] | 0.1kWh | [5 empty] | SPA used System electric energy today H
1138 |  |  |  | Esystem_ today L | [10 empty] | System electric energy today L | [23 empty] | 0.1kWh | [5 empty] | SPA used System electric energy today L
1139 |  |  |  | Esystem_total H | [10 empty] | System electric energy total H | [23 empty] | 0.1kWh | [5 empty] | SPA used System electric energy total H
1140 |  |  |  | Esystem_ total L | [10 empty] | System electric energy total L | [23 empty] | 0.1kWh | [5 empty] | SPA used System electric energy total L
…… |  |  |  | / | [10 empty] | / | [16 empty] | / | [6 empty] | / | [5 empty] | reversed
1249 |  |  |  | / | [10 empty] | / | [16 empty] | / | [6 empty] | / | [5 empty] | reversed
Tenth group for Storage power(历史信息查询，存在本地 EEPROM 中) no use
1250 |  |  |  | Ec_ day0 H | [10 empty] | Energy Charge of latest day | [23 empty] | 0.1kwh | [5 empty] | No use
1251 |  |  |  | Ec_day0 L | [10 empty] | Energy Charge of latest day | [23 empty] | 0.1kwh | [5 empty] | No use
1252 |  |  |  | Ec_ day1 H | [10 empty] | Energy Charge of latest 1st day | [23 empty] | 0.1kwh
1253 |  |  |  | Ec_ day1 L | [10 empty] | Energy Charge of latest 1st day | [23 empty] | 0.1kwh
… |  |  |  | Ec_ day | [10 empty] | … | [23 empty] | 0.1kwh
… |  |  |  | Ec_ day | [10 empty] | … | [23 empty] | 0.1kwh
…. |  |  |  | Ec_ day 6 H | [10 empty] | Energy Charge of latest 6th day | [23 empty] | 0.1kwh
1261 |  |  |  | Ec_ day 6L | [10 empty] | Energy Charge of latest 6th day | [23 empty] | 0.1kwh
1262 |  |  |  | Ec_ month0 H | [10 empty] | Energy Charge of latest month | [23 empty] | 0.1kwh
1263 |  |  |  | Ec_ month0 L | [10 empty] | Energy Charge of latest month | [23 empty] | 0.1kwh
1264 |  |  |  | Ec_ month1 H | [10 empty] | Energy Charge of latest 1st month | [23 empty] | 0.1kwh
1265 |  |  |  | Ec_ month1 L | [10 empty] | Energy Charge of latest 1st month | [23 empty] | 0.1kwh
… |  |  |  | Ec_ month | [10 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
… |  |  |  | Ec_ month | [10 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
1284 |  |  |  | Ec_ month11 H | [10 empty] | Energy Charge of latest 11th month | [23 empty] | 0.1kwh
1285 |  |  |  | Ec_ month11L | [10 empty] | Energy Charge of latest 11th month | [23 empty] | 0.1kwh
1286 |  |  |  | Ec_ year0 H | [10 empty] | Energy Charge of latest year | [23 empty] | 0.1kwh
1287 |  |  |  | Ec_ year 0 L | [10 empty] | Energy Charge of latest year | [23 empty] | 0.1kwh
1288 |  |  |  | Ed_ day0 H | [10 empty] | Energy Disharge of latest day | [23 empty] | 0.1kwh
1289 |  |  |  | Ed_day0 L | [10 empty] | Energy Disharge of latest day | [23 empty] | 0.1kwh
1290 |  |  |  | Ed_ day1 H | [10 empty] | Energy Disharge of latest 1st day | [23 empty] | 0.1kwh
1291 |  |  |  | Ed_ day1 L | [10 empty] | Energy Disharge of latest 1st day | [23 empty] | 0.1kwh
… |  |  |  | Ed_ day | [10 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
… |  |  |  | Ed_ day | [10 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
1298 |  |  |  | Ed_ day 6 H | [10 empty] | Energy Disharge of latest 6th day | [23 empty] | 0.1kwh | [5 empty] | No use
1299 |  |  |  | Ed_ day 6L | [10 empty] | Energy Disharge of latest 6th day | [23 empty] | 0.1kwh | [5 empty] | No use
1300 |  |  |  | Ed_ month0 H | [10 empty] | Energy Disharge of latest month | [23 empty] | 0.1kwh | [5 empty] | No use
1301 |  |  |  | Ed_ month0 L | [10 empty] | Energy Disharge of latest month | [23 empty] | 0.1kwh | [5 empty] | No use
1302 |  |  |  | Ed_ month1 H | [10 empty] | Energy Disharge of latest 1st month | [23 empty] | 0.1kwh | [5 empty] | No use
1303 |  |  |  | Ed_ month1 L | [10 empty] | Energy Disharge of latest 1st month | [23 empty] | 0.1kwh | [5 empty] | No use
… |  |  |  | Ed_ month | [10 empty] | … | [23 empty] | 0.1kwh
… |  |  |  | Ed_ month | [10 empty] | … | [23 empty] | 0.1kwh
1322 |  |  |  | Ed_ month11 H | [10 empty] | Energy Disharge of latest 11th month | [23 empty] | 0.1kwh
1323 |  |  |  | Ed_ month11L | [10 empty] | Energy Disharge of latest 11th month | [23 empty] | 0.1kwh
1324 |  |  |  | Ed_ year0 H | [10 empty] | Energy Disharge of latest year | [23 empty] | 0.1kwh
1325 |  |  |  | Ed_ year 0 L | [10 empty] | Energy Disharge of latest year | [23 empty] | 0.1kwh
1326 |  |  |  | Eg_ day0 H | [10 empty] | Energy to grid of latest day | [23 empty] | 0.1kwh
1327 |  |  |  | Eg_day0 L | [10 empty] | Energy to grid of latest day | [23 empty] | 0.1kwh
1328 |  |  |  | Eg_ day1 H | [10 empty] | Energy to grid of latest 1st day | [23 empty] | 0.1kwh
1329 |  |  |  | Eg_ day1 L | [10 empty] | Energy to grid of latest 1st day | [23 empty] | 0.1kwh
… |  |  |  | Eg_ day | [10 empty] | … | [23 empty] | 0.1kwh
… |  |  |  | Eg_ day | [10 empty] | … | [23 empty] | 0.1kwh
1337 |  |  |  | Eg_ day 6 H | [10 empty] | Energy to grid of latest 6th day | [23 empty] | 0.1kwh
1338 |  |  |  | Eg_ day 6L | [10 empty] | Energy to grid of latest 6th day | [23 empty] | 0.1kwh
1339 |  |  | Eg_ month0 H | [11 empty] | Energy to grid of latest month | [23 empty] | 0.1kwh
1340 |  |  | Eg_ month0 L | [11 empty] | Energy to grid of latest month | [23 empty] | 0.1kwh
1341 |  |  | Eg_ month1 H | [11 empty] | Energy to grid of latest 1st month | [23 empty] | 0.1kwh
1342 |  |  | Eg_ month1 L | [11 empty] | Energy to grid of latest 1st month | [23 empty] | 0.1kwh
… |  |  | Eg_ month | [11 empty] | … | [23 empty] | 0.1kwh
… |  |  | Eg_ month | [11 empty] | … | [23 empty] | 0.1kwh
1361 |  |  | Eg_ month11 H | [11 empty] | Energy month |  |  |  | to grid of | [5 empty] | latest 11th | [13 empty] | 0.1kwh
1362 |  |  | Eg_ month11L | [11 empty] | Energy month |  |  |  | to grid of | [5 empty] | latest 11th | [13 empty] | 0.1kwh
1363 |  |  | Eg_ year0 H | [11 empty] | Energy to grid of latest year | [23 empty] | 0.1kwh
1364 |  |  | Eg_ year 0 L | [11 empty] | Energy to grid of latest year | [23 empty] | 0.1kwh
1365 |  |  | Eu_ day0 H | [11 empty] | Energy to user of latest day | [23 empty] | 0.1kwh
1366 |  |  | Eu_day0 L | [11 empty] | Energy to user of latest day | [23 empty] | 0.1kwh | [5 empty] | No use
1367 |  |  | Eu_ day1 H | [11 empty] | Energy to user of latest 1st day | [23 empty] | 0.1kwh | [5 empty] | No use
1368 |  |  | Eu_ day1 L | [11 empty] | Energy to user of latest 1st day | [23 empty] | 0.1kwh | [5 empty] | No use
… |  |  | Eu_ day | [11 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
… |  |  | Eu_ day | [11 empty] | … | [23 empty] | 0.1kwh | [5 empty] | No use
Eleventh group for Storage power no use
1375 |  |  | Eu_ day 6 H | [11 empty] | Energy to user of latest 6th day | [23 empty] | 0.1kwh | [5 empty] | No use
1376 |  |  | Eu_ day 6L | [11 empty] | Energy to user of latest 6th day | [23 empty] | 0.1kwh
1377 |  |  | Eu_ month0 H | [11 empty] | Energy to user of latest month | [23 empty] | 0.1kwh
1378 |  |  | Eu_ month0 L | [11 empty] | Energy to user of latest month | [23 empty] | 0.1kwh
1379 |  |  | Eu_ month1 H | [11 empty] | Energy to user of latest 1st month | [23 empty] | 0.1kwh
1380 |  |  | Eu_ month1 L | [11 empty] | Energy to user of latest 1st month | [23 empty] | 0.1kwh
… |  |  | Eu_ month | [11 empty] | … | [23 empty] | 0.1kwh
… |  |  | Eu_ month | [11 empty] | … | [23 empty] | 0.1kwh
1399 |  |  | Eu_ month11 H | [11 empty] | Energy to user of latest 11th month | [23 empty] | 0.1kwh
1400 |  |  | Eu_ month11L | [11 empty] | Energy to user of latest 11th month | [23 empty] | 0.1kwh
1401 |  |  | Eu_ year0 H | [11 empty] | Energy to user of latest year | [23 empty] | 0.1kwh
1402 |  |  | Eu_ year 0 L | [11 empty] | Energy to user of latest year | [23 empty] | 0.1kwh
Twelfth group for buck-boost debug no use
1500 |  |  | CurrentRecord_0x 22 | [11 empty] | OCD Date & Time(L) R | [16 empty] | 0-5:Second 6-11:minute 12-16:hour 17-21:day 22-25:month 26-31:year | [12 empty] | No use
1501 |  |  | CurrentRecord_0x 23 | [11 empty] | OCD Date & Time(H) | [11 empty] | R
1502 |  |  | CurrentRecord_0x 24 | [11 empty] | Current SCD Protection Counts in Discharge | [11 empty] | R |  |  |  |  | 0-65534
1503 |  |  | CurrentRecord_0x 25 | [11 empty] | SCD Date & Time(L) | [11 empty] | R |  |  |  |  | 0-5:Second 6-11:minute 12-16:hour 17-21:day 22-25:month 26-31:year
1504 |  |  | CurrentRecord_0x 26 | [11 empty] | SCD Date & Time(H) | [11 empty] | R
1505 |  |  | CurrentRecordUp date | [23 empty] | R |  |  |  |  | 0: unrefreshed 1: refreshed
1506 |  |  | CurrentRecord_0x 28 | [23 empty] | R |  |  |  |  | reversed | [12 empty] | No use
1507 |  |  | CurrentRecord_0x 29 | [23 empty] | R |  |  |  |  | reversed
1508 |  |  | CurrentRecord_0x 2A | [23 empty] | R |  |  |  |  | reversed
1509 |  |  | CurrentRecord_0x 2B | [23 empty] | R |  |  |  |  | reversed
1510 |  |  | CurrentRecord_0x 2C | [23 empty] | R |  |  |  |  | reversed
1511 |  |  | CurrentRecord_0x 2D | [23 empty] | R |  |  |  |  | reversed
1512 |  |  | CurrentRecord_0x 2E | [23 empty] | R |  |  |  |  | reversed
1513 |  |  | CurrentRecord_0x 2F | [23 empty] | R |  |  |  |  | reversed
1514 |  |  | VoltageRecord_0x 31 | [11 empty] | High Voltage Protection Counts in Charge | [11 empty] | R | [17 empty] | No use
1515 |  |  | VoltageRecord_0x 32 | [11 empty] | High Voltage Protection Counts in Discharge | [11 empty] | R
1516 |  |  | VoltageRecord_0x 33 | [11 empty] | OVC Date & Time(L) | [11 empty] | R
1517 |  |  | VoltageRecord_0x 34 | [11 empty] | OVC Date & Time(H) | [11 empty] | R
1518 |  |  | VoltageRecord_0x | [11 empty] | OVD Date & Time(L)
35
1519 |  |  | VoltageRecord_0x 36 | [11 empty] | OVD Date & Time(H)
1520 |  |  | VoltageRecord_0x 37 | [11 empty] | Low Voltage Protection Counts in Charge
1521 |  |  | VoltageRecord_0x 38 | [11 empty] | Low Voltage Protection Counts in Discharge
1522 |  |  | VoltageRecord_0x 39 | [11 empty] | UVC Date & Time(L)
1523 |  |  | VoltageRecord_0x 3A | [11 empty] | UVC Date & Time(H)
1524 |  |  | VoltageRecord_0x 3B | [11 empty] | UVD Date & Time(L)
1525 |  |  | VoltageRecord_0x 3C | [11 empty] | UVD Date & Time(H)
1526 |  |  | VoltageRecordUp date | [28 empty] | 0: unrefreshed 1: refreshed
1527 |  |  | VoltageRecord_0x 3E | [28 empty] | reversed
1528 |  |  | VoltageRecord_0x 3F | [28 empty] | reversed
1529 |  |  | TemperatureRecor d_0x41 | [11 empty] | High Temperature Protection Counts in Charge
1530 |  |  | TemperatureRecor d_0x42 | [11 empty] | High Temperature Protection Counts in Discharge
1531 |  |  | TemperatureRecor d_0x43 | [11 empty] | OTC Date & Time(L)
1532 |  |  | TemperatureRecor d_0x44 | [11 empty] | OTC Date & Time(H) | [29 empty] | No use
1533 |  |  | TemperatureRecor d_0x45 | [11 empty] | OTD Date & Time(L)
1534 |  |  | TemperatureRecor d_0x46 | [11 empty] | OTD Date & Time(H)
1535 |  |  | TemperatureRecor d_0x47 | [11 empty] | Low Temperature Protection Counts in Charge
1536 |  |  | TemperatureRecor d_0x48 | [11 empty] | Low Temperature Protection Counts in Discharge
1537 |  |  | TemperatureRecor d_0x49 | [11 empty] | UTC Date & Time(L)
1538 |  |  | TemperatureRecor d_0x4A | [11 empty] | UTC Date & Time(H)
1539 |  |  | TemperatureRecor d_0x4B | [11 empty] | UTD Date & Time(L)
1540 |  |  | TemperatureRecor d_0x4C | [11 empty] | UTD Date & Time(H)
1541 |  |  | TemperatureRecor dUpdate | [28 empty] | reversed | [6 empty] | 0: unrefres hed 1: refreshed
1542 |  |  | TemperatureRecor d_0x4E | [28 empty] | reversed | [12 empty] | No use
1543 |  |  | TemperatureRecor d_0x4F | [28 empty] | reversed
1544 |  |  | ChargeRecordUpd ate | [23 empty] | W/R |  |  |  |  | 0: unrefreshed 1: refreshed | [6 empty] | default:0
1545 |  |  | ChargeRecord_0x 51 | [11 empty] | Charge Counts (more than 60s) | [16 empty] | 0~65534
1546 |  |  | ChargeRecord_0x 52 | [11 empty] | Last charge Date & Time(L)
1547 |  |  | ChargeRecord_0x 53 | [11 empty] | Last charge Date & Time(H)
1548 |  |  | ChargeRecord_0x 54 | [11 empty] | Full Charge Counts | [16 empty] | 0~65534
1549 |  |  | ChargeRecord_0x 55 | [11 empty] | Last full charge Date & Time(L) | [29 empty] | No use
1550 |  |  | ChargeRecord_0x 56 | [11 empty] | Last full charge Date & Time(H)
1551 |  |  | ChargeRecord_0x 57 | [11 empty] | 2nd Protection Active Date & Time(L)
1552 |  |  | ChargeRecord_0x 58 | [11 empty] | 2nd Protection Active Date & Time(H)
1553 |  |  | ChargeRecord_0x 59 | [28 empty] | reversed
1554 |  |  | ChargeRecord_0x 5A | [28 empty] | reversed
1555 |  |  | StatusInfo_0x11 | [11 empty] | Date&Time(L)
1556 |  |  | StatusInfo_0x12 | [11 empty] | Date&Time(H)
1557 |  |  | StatusInfo_0x13 | [11 empty] | status | [16 empty] | bit0-1:00-pre -charge; 01-standby; 10-charging; 11-dischargi ng bit2: 0-no error; 1-error bit3: 0-unbalanc; 1-balance bit4: 0-wake; 1-sleep bit5: 0-mosfet off; 1-mosfet on bit6-8:revers ed
1558 |  |  | StatusInfo_0x14 | [11 empty] | Error code | [16 empty] | bit0: OCD bit1: SCD bit2: OV bit3: UV bit4: OTD bit5: OTC bit6: UTD bit7: UTC
1559 |  |  | StatusInfo_0x15 | [11 empty] | SOC | [16 empty] | 0-100 | [6 empty] | % | [5 empty] | No use
1560 |  |  | StatusInfo_0x16 | [11 empty] | Voltage | [23 empty] | 10mV
1561 |  |  | StatusInfo_0x17 | [11 empty] | Current | [23 empty] | 10mA
1562 |  |  | StatusInfo_0x18 | [11 empty] | Temperature | [16 empty] | -127~127 | [6 empty] | ℃
1563 |  |  | StatusInfo_0x19 | [11 empty] | Max. charge current | [23 empty] | 10mA
1564 |  |  | BMSCompany | [11 empty] | BMS company from BMS | [16 empty] | 0:Darfon 1:Pace | [6 empty] | FF
1565 |  |  | Discharge power limit | [11 empty] | power limit for discharge(only Read) | [11 empty] | W |  |  |  |  | 0-100 | [6 empty] | percenta ge
100
1566 |  |  | Charge power limit | [11 empty] | power limit for charge(only read) | [11 empty] | W |  |  |  |  | 0-100 | [6 empty] | percenta ge 100
1567 |  |  | Bat temp limit Hysteresis | [28 empty] | 0-110:0-11 ℃ | [6 empty] | 0.1℃
1568 |  |  | DischargeToStand | [11 empty] | Reason of state change | [13 empty] | 1:Due to flash
|  |  | byReason | [11 empty] | from discharge to standby | [13 empty] | 2:Due to fault
3:PV and AC voltage
both too low to
support SPS
4:PV voltage high
for discharge
5:Battery voltage
low for discharge
6:Power to user low
for discharge
7: AC State change
8: turn off order
9: Bat temp out of
range
10: MPPT Trouble
11: forbid by BMS
1569 |  |  | ChargeToStandby | [11 empty] | Reason of state change | [13 empty] | 1:Due to flash | [15 empty] | DEBUG
|  |  | Reason | [11 empty] | from charge to standby | [13 empty] | 2:Due to fault
3:PV and AC voltage
both too low to
support SPS
4:PV voltage low for
charge
5:Battery voltage
high for charge
6:PV power low for
charge
7: AC State change
8: turn off order
9: Bat temp out of
range
10: MPPT Trouble
11: forbid by BMS
12: PV volt high for
charge
13: Over current detected 14: BUS voltage high 15: bus2 voltage softstart fail.
1570
1571
….. |  |  | 1572~1999
thirteen group for Storage power’s SPA
2000 |  |  |  | Inverter Status | [10 empty] | Inverter run state | [18 empty] | 0:waiting, 1:normal, 3:fault | [11 empty] | SPA
2001 |  |  |  | Ppv H | [10 empty] | Input power (high) | [25 empty] | 0.1W
2002 |  |  |  | Ppv L | [10 empty] | Input power (low) | [25 empty] | 0.1W
2003 |  |  |  | Vpv1 | [10 empty] | PV1 voltage | [25 empty] | 0.1V
2004 |  |  |  | PV1Curr | [10 empty] | PV1 input current | [25 empty] | 0.1A
2005 |  |  |  | Ppv1 H | [10 empty] | PV1 input power(high) | [25 empty] | 0.1W
2006 |  |  |  | Ppv1 L | [10 empty] | PV1 input power(low) | [25 empty] | 0.1W
2007 |  |  |  | Vpv2 | [10 empty] | PV2 voltage | [25 empty] | 0.1V
2008 |  |  |  | PV2Curr | [10 empty] | PV2 input current | [25 empty] | 0.1A
2009 |  |  |  | Ppv2 H | [10 empty] | PV2 input power (high) | [25 empty] | 0.1W
2010 |  |  |  | Ppv2 L | [10 empty] | PV2 input power (low) | [25 empty] | 0.1W
2011 |  |  |  | Vpv3 | [10 empty] | PV3 voltage | [25 empty] | 0.1V
2012 |  |  |  | PV3Curr | [10 empty] | PV3 input current | [25 empty] | 0.1A
2013 |  |  |  | Ppv3 H | [10 empty] | PV3 input power (high) | [25 empty] | 0.1W
2014 |  |  |  | Ppv3 L | [10 empty] | PV3 input power (low) | [25 empty] | 0.1W
2015 |  |  |  | Vpv4 | [10 empty] | PV4 voltage | [25 empty] | 0.1V
2016 |  |  |  | PV4Curr | [10 empty] | PV4 input current | [25 empty] | 0.1A
2017 |  |  |  | Ppv4 H | [10 empty] | PV4 input power (high) | [25 empty] | 0.1W
2018 |  |  |  | Ppv4 L | [10 empty] | PV4 input power (low) | [25 empty] | 0.1W
2019 |  |  |  | Vpv5 | [10 empty] | PV5 voltage | [25 empty] | 0.1V
2020 |  |  |  | PV5Curr | [10 empty] | PV5 input current | [25 empty] | 0.1A
2021 |  |  |  | Ppv5H | [10 empty] | PV5 input power(high) | [25 empty] | 0.1W
2022 |  |  |  | Ppv5 L | [10 empty] | PV5 input power(low) | [25 empty] | 0.1W
2023 |  |  |  | Vpv6 | [10 empty] | PV6 voltage | [25 empty] | 0.1V
2024 |  |  |  | PV6Curr | [10 empty] | PV6 input current | [25 empty] | 0.1A
2025 |  |  |  | Ppv6 H | [10 empty] | PV6 input power (high) | [25 empty] | 0.1W
2026 |  |  |  | Ppv6 L | [10 empty] | PV6 input power (low) | [25 empty] | 0.1W
2027 |  |  |  | Vpv7 | [10 empty] | PV7 voltage | [25 empty] | 0.1V
2028 |  |  |  | PV7Curr | [10 empty] | PV7 input current | [25 empty] | 0.1A
2029 |  |  |  | Ppv7 H | [10 empty] | PV7 input power (high) | [25 empty] | 0.1W
2030 |  |  |  | Ppv7 L | [10 empty] | PV7 input power (low) | [25 empty] | 0.1W
2031 |  |  |  | Vpv8 | [10 empty] | PV8 voltage | [25 empty] | 0.1V
2032 |  |  |  | PV8Curr | [10 empty] | PV8 input current | [25 empty] | 0.1A
2033 |  |  |  | Ppv8 H | [10 empty] | PV8 input power (high) | [25 empty] | 0.1W
2034 |  |  |  | Ppv8 L | [10 empty] | PV8 input power (low) | [25 empty] | 0.1W
2035 |  |  |  | Pac H | [10 empty] | Output power (high) | [25 empty] | 0.1W |  |  |  |  | SPA
2036 |  |  |  | Pac L | [10 empty] | Output power (low) | [25 empty] | 0.1W |  |  |  |  | SPA
2037 |  |  |  | Fac | [10 empty] | Grid frequency | [25 empty] | 0.01Hz |  |  |  |  | SPA
2038 |  |  |  | Vac1 | [10 empty] | Three/single phase grid voltage | [25 empty] | 0.1V |  |  |  |  | SPA
2039 |  |  |  | Iac1 | [10 empty] | Three/single phase grid output current | [25 empty] | 0.1A |  |  |  |  | SPA
2040 |  |  |  | Pac1 H | [10 empty] | Three/single phase grid output watt VA (high) | [25 empty] | 0.1VA |  |  |  |  | SPA
2041 |  |  |  | Pac1 L | [10 empty] | Three/single phase grid output watt VA(low) | [25 empty] | 0.1VA |  |  |  |  | SPA
2042 |  |  |  | Vac2 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
2043 |  |  |  | Iac2 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A
2044 |  |  |  | Pac2 H | [10 empty] | Three phase grid output power (high) | [25 empty] | 0.1VA
2045 |  |  |  | Pac2 L | [10 empty] | Three phase grid output power (low) | [25 empty] | 0.1VA
2046 |  |  |  | Vac3 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
2047 |  |  |  | Iac3 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A
2048 |  |  |  | Pac3 H | [10 empty] | Three phase grid output power (high) | [25 empty] | 0.1VA
2049 |  |  |  | Pac3 L | [10 empty] | Three phase grid output power (low) | [25 empty] | 0.1VA
2050 |  |  |  | Vac_RS | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
2051 |  |  |  | Vac_ST | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
2052 |  |  |  | Vac_TR | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Line voltage
2053 |  |  |  | Eac today H | [10 empty] | Today generate energy (high) | [25 empty] | 0.1kWH |  |  |  |  | SPA
2054 |  |  |  | Eac today L | [10 empty] | Today generate energy (low) | [25 empty] | 0.1kWH |  |  |  |  | SPA
2055 |  |  |  | Eac total H | [10 empty] | Total generate energy (high) | [25 empty] | 0.1kWH |  |  |  |  | SPA
2056 |  |  |  | Eac total L | [10 empty] | Total generate energy (low) | [25 empty] | 0.1kWH |  |  |  |  | SPA
2057 |  |  |  | Time total H | [10 empty] | Work time total (high) | [25 empty] | 0.5s |  |  |  |  | SPA
2058 |  |  |  | Time total L | [10 empty] | Work time total (low) | [25 empty] | 0.5s |  |  |  |  | SPA
2059 |  |  |  | Epv1_today H | [10 empty] | PV1 Energy today (high) | [25 empty] | 0.1kWh
2060 |  |  |  | Epv1_today L | [10 empty] | PV1 Energy today (low) | [25 empty] | 0.1kWh
2061 |  |  |  | Epv1_total H | [10 empty] | PV1 Energy total (high) | [25 empty] | 0.1kWh
2062 |  |  |  | Epv1_total L | [10 empty] | PV1 Energy total (low) | [25 empty] | 0.1kWh
2063 |  |  |  | Epv2_today H | [10 empty] | PV2 Energy today (high) | [25 empty] | 0.1kWh
2064 |  |  |  | Epv2_today L | [10 empty] | PV2 Energy today (low) | [25 empty] | 0.1kWh
2065 |  |  |  | Epv2_total H | [10 empty] | PV2 Energy total (high) | [25 empty] | 0.1kWh
2066 |  |  |  | Epv2_total L | [10 empty] | PV2 Energy total (low) | [25 empty] | 0.1kWh
2067 |  |  |  | Epv3_today H | [10 empty] | PV3 Energy today (high) | [25 empty] | 0.1kWh
2068 |  |  |  | Epv3_today L | [10 empty] | PV3 Energy today (low) | [25 empty] | 0.1kWh
2069 |  |  |  | Epv3_total H | [10 empty] | PV3 Energy total (high) | [25 empty] | 0.1kWh
2070 |  |  |  | Epv3_total L | [10 empty] | PV3 Energy total (low) | [25 empty] | 0.1kWh
2071 |  |  |  | Epv4_today H | [10 empty] | PV4 Energy today (high) | [25 empty] | 0.1kWh
2072 |  |  |  | Epv4_today L | [10 empty] | PV4 Energy today (low) | [25 empty] | 0.1kWh
2073 |  |  |  | Epv4_total H | [10 empty] | PV4 Energy total (high) | [25 empty] | 0.1kWh
2074 |  |  |  | Epv4_total L | [10 empty] | PV4 Energy total (low) | [25 empty] | 0.1kWh
2075 |  |  |  | Epv5_today H | [10 empty] | PV5 Energy today (high) | [25 empty] | 0.1kWh
2076 |  |  |  | Epv5_today L | [10 empty] | PV5 Energy today (low) | [25 empty] | 0.1kWh
2077 |  |  |  | Epv5_total H | [10 empty] | PV5 Energy total (high) | [25 empty] | 0.1kWh
2078 |  |  |  | Epv5_total L | [10 empty] | PV5 Energy total (low) | [25 empty] | 0.1kWh
2079 |  |  |  | Epv6_today H | [10 empty] | PV6 Energy today (high) | [25 empty] | 0.1kWh
2080 |  |  |  | Epv6_today L | [10 empty] | PV6Energy today (low) | [25 empty] | 0.1kWh
2081 |  |  |  | Epv6_total H | [10 empty] | PV6 Energy total (high) | [25 empty] | 0.1kWh
2082 |  |  |  | Epv6_total L | [10 empty] | PV6 Energy total (low) | [25 empty] | 0.1kWh
2083 |  |  |  | Epv7_today H | [10 empty] | PV7 Energy today (high) | [25 empty] | 0.1kWh
2084 |  |  |  | Epv7_today L | [10 empty] | PV7 Energy today (low) | [25 empty] | 0.1kWh
2085 |  |  |  | Epv7_total H | [10 empty] | PV7 Energy total (high) | [25 empty] | 0.1kWh
2086 |  |  |  | Epv7_total L | [10 empty] | PV7 Energy total (low) | [25 empty] | 0.1kWh
2087 |  |  |  | Epv8_today H | [10 empty] | PV8 Energy today (high) | [25 empty] | 0.1kWh
2088 |  |  |  | Epv8_today L | [10 empty] | PV8Energy today (low) | [25 empty] | 0.1kWh
2089 |  |  |  | Epv8_total H | [10 empty] | PV8 Energy total (high) | [25 empty] | 0.1kWh
2090 |  |  |  | Epv8_total L | [10 empty] | PV8 Energy total (low) | [25 empty] | 0.1kWh
2091 |  |  |  | Epv_total H | [10 empty] | PV Energy total (high) | [25 empty] | 0.1kWh
2092 |  |  |  | Epv_total L | [10 empty] | PV Energy total (low) | [25 empty] | 0.1kWh
2093 |  |  |  | Temp1 | [10 empty] | Inverter temperature | [25 empty] | 0.1C |  |  |  |  | SPA
2094 |  |  |  | Temp2 | [10 empty] | The inside IPM in inverter Temperature | [25 empty] | 0.1C |  |  |  |  | SPA
2095 |  |  |  | Temp3 | [10 empty] | Boost temperature | [25 empty] | 0.1C |  |  |  |  | SPA
2096 |  |  |  | Temp4 | [41 empty] | reserved
2097 |  |  |  | uwBatVolt_DSP | [10 empty] | BatVolt_DSP | [25 empty] | 0.1V |  |  |  |  | BatVolt(DSP)
2098 |  |  |  | P Bus Voltage | [10 empty] | P Bus inside Voltage | [25 empty] | 0.1V |  |  |  |  | SPA
2099 |  |  |  | N Bus Voltage | [10 empty] | N Bus inside Voltage | [25 empty] | 0.1V |  |  |  |  | SPA
2100 |  |  |  | RemoteCtrlEn | [10 empty] | / | [18 empty] | 0.Load First 1.BatFirst 2.Grid | [6 empty] | / |  |  |  |  | Remote setup enable
2101 |  |  |  | RemoteCtrlPow er | [10 empty] | / | [25 empty] | / |  |  |  |  | Remotely set power
2102 |  |  |  | Extra AC Power to grid_H | [10 empty] | Extra inverte AC Power to grid High | [18 empty] | For SPA connect inverter | [11 empty] | SPA used
2103 |  |  |  | Extra AC Power to grid_L | [10 empty] | Extrainverte AC Power to grid Low | [30 empty] | SPA used
2104 |  |  |  | Eextra_today H | [10 empty] | Extra inverter PowerTOUser_Extra today (high) | [18 empty] | R | [6 empty] | 0.1kWh |  |  |  |  | SPA used
2105 |  |  |  | Eextra_today L | [10 empty] | Extra inverter PowerTOUser_Extra today (low) | [18 empty] | R | [6 empty] | 0.1kWh |  |  |  |  | SPA used
2106 |  |  |  | Eextra_total H | [10 empty] | Extra inverter PowerTOUser_Extratotal(high) | [25 empty] | 0.1kWh |  |  |  |  | SPA used
2107 |  |  |  | Eextra_total L | [10 empty] | Extra inverter PowerTOUser_Extra total(low) | [25 empty] | 0.1kWh |  |  |  |  | SPA used
2108 |  |  |  | Esystem_today H | [10 empty] | System electric energy today H | [25 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today H
2109 |  |  |  | Esystem_ today L | [10 empty] | System electric energy today L | [25 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today L
2110 |  |  |  | Esystem_total H | [10 empty] | System electric energy total H | [25 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy total H
2111 |  |  |  | Esystem_ total L | [10 empty] | System electric energy total L | [25 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy total L
2112 |  |  |  | EACharge_Today _H | [10 empty] | ACCharge energy today | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
2113 |  |  |  | EACharge_Today _L | [10 empty] | ACCharge energy today | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
2114 |  |  |  | EACharge_Total _H | [10 empty] | ACCharge energy total | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
2115 |  |  |  | EACharge_Total _L | [10 empty] | ACCharge energy total | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
2116 |  |  |  | AC charge | [10 empty] | Grid power to local load | [25 empty] | 0.1kwh |  |  |  |  | Storage
|  |  |  | Power_H | [41 empty] | Power
2117 |  |  |  | AC charge Power_L | [10 empty] | Grid power to local load | [25 empty] | 0.1kwh |  |  |  |  | Storage Power
2118 |  |  |  | Priority | [10 empty] | 0:Load First 1:Battery First 2:Grid First | [30 empty] | Storage Power
2119 |  |  |  | Battery Type | [10 empty] | 0：Lead-acid 1：Lithium battery | [30 empty] | Storage Power
2120 |  |  |  | AutoProofreadC MD | [10 empty] | Aging mode | [30 empty] | Storage Power
… |  |  |  | reserved | [41 empty] | reserved
2124 |  |  |  | reserved | [41 empty] | reserved
Use for TL-X and TL-XH
3000 |  |  |  | Inverter Status | [10 empty] | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: 自检模式，可选 2: Reserved 3：SysFault module 4: Flash module 5：PVBATOnline module: 6：BatOnline module 7：PVOfflineMode 8：BatOfflineMode 低 8 位表示机器状态（网页显示） 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus;
3001 |  |  |  | Ppv H | [10 empty] | PV total power | [25 empty] | 0.1W
3002 |  |  |  | Ppv L
3003 |  |  |  | Vpv1 | [10 empty] | PV1 voltage | [25 empty] | 0.1V
3004 |  |  |  | Ipv1 | [10 empty] | PV1 input current | [25 empty] | 0.1A
3005 |  |  |  | Ppv1 H | [10 empty] | PV1 power | [25 empty] | 0.1W
3006 |  |  |  | Ppv1 L
3007 |  |  |  | Vpv2 | [10 empty] | PV2 voltage | [25 empty] | 0.1V
3008 |  |  |  | Ipv2 | [10 empty] | PV2 input current | [25 empty] | 0.1A
3009 |  |  |  | Ppv2 H | [10 empty] | PV2 power | [25 empty] | 0.1W
3010 |  |  |  | Ppv2 L
3011 |  |  |  | Vpv3 | [10 empty] | PV3 voltage | [25 empty] | 0.1V
3012 |  |  |  | Ipv3 | [10 empty] | PV3 input current | [25 empty] | 0.1A
3013 |  |  |  | Ppv3 H | [10 empty] | PV3 power | [25 empty] | 0.1W
3014 |  |  |  | Ppv3 L
3015 |  |  |  | Reserved
3016 |  |  |  | Reserved
3017 |  |  |  | Reserved
3018 |  |  |  | Reserved
3019 |  |  |  | Reserved
3020 |  |  |  | Reserved
3021 |  |  |  | Reserved
3022 |  |  |  | Reserved
3023 |  |  |  | Pac H | [10 empty] | Output power | [25 empty] | 0.1W |  |  |  |  | Output power
3024 |  |  |  | Pac L
3025 |  |  |  | Fac | [10 empty] | Grid frequency | [25 empty] | 0.01Hz |  |  |  |  | Grid frequency
3026 |  |  |  | Vac1 | [10 empty] | Three/single phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Three/single phase grid voltage
3027 |  |  |  | Iac1 | [10 empty] | Three/single phase grid output current | [25 empty] | 0.1A |  |  |  |  | Three/single phase grid output current
3028 |  |  |  | Pac1 H | [10 empty] | Three/single phase grid output watt VA | [25 empty] | 0.1VA |  |  |  |  | Three/single phase grid output watt VA
3029 |  |  |  | Pac1 L
3030 |  |  |  | Vac2 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Three phase grid voltage
3031 |  |  |  | Iac2 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A |  |  |  |  | Three phase grid output current
3032 |  |  |  | Pac2 H | [10 empty] | Three phase grid output power | [25 empty] | 0.1VA |  |  |  |  | Three phase grid output power
3033 |  |  |  | Pac2 L
3034 |  |  |  | Vac3 | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V |  |  |  |  | Three phase grid voltage
3035 |  |  |  | Iac3 | [10 empty] | Three phase grid output current | [25 empty] | 0.1A |  |  |  |  | Three phase grid output current
3036 |  |  |  | Pac3 H | [10 empty] | Three phase grid output power | [25 empty] | 0.1VA |  |  |  |  | Three phase
3037 |  |  |  | Pac3 L | [41 empty] | grid output power
3038 |  |  |  | Vac_RS | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
3039 |  |  |  | Vac_ST | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
3040 |  |  |  | Vac_TR | [10 empty] | Three phase grid voltage | [25 empty] | 0.1V
3041 |  |  |  | Ptouser total H | [10 empty] | Total forward power | [25 empty] | 0.1W |  |  |  |  | Total forward power
3042 |  |  |  | Ptouser total L
3043 |  |  |  | Ptogrid total H | [10 empty] | Total reverse power | [25 empty] | 0.1W |  |  |  |  | Total reverse power
3044 |  |  |  | Ptogrid total L
3045 |  |  |  | Ptoload total H | [10 empty] | Total load power | [25 empty] | 0.1W |  |  |  |  | Total load power
3046 |  |  |  | Ptoload total L
3047 |  |  |  | Time total H | [10 empty] | Work time total | [25 empty] | 0.5s
3048 |  |  |  | Time total L
3049 |  |  |  | Eac today H | [10 empty] | Today generate energy | [25 empty] | 0.1kWh |  |  |  |  | Today generate energy
3050 |  |  |  | Eac today L
3051 |  |  |  | Eac total H | [10 empty] | Total generate energy | [25 empty] | 0.1kWh |  |  |  |  | Total generate energy
3052 |  |  |  | Eac total L
3053 |  |  |  | Epv_total H | [10 empty] | PV energy total | [25 empty] | 0.1kWh |  |  |  |  | PV energy total
3054 |  |  |  | Epv_total L
3055 |  |  |  | Epv1_today H | [10 empty] | PV1 energy today | [25 empty] | 0.1kWh
3056 |  |  |  | Epv1_today L
3057 |  |  |  | Epv1_total H | [10 empty] | PV1 energy total | [25 empty] | 0.1kWh
3058 |  |  |  | Epv1_total L
3059 |  |  |  | Epv2_today H | [10 empty] | PV2 energy today | [25 empty] | 0.1kWh
3060 |  |  |  | Epv2_today L
3061 |  |  |  | Epv2_total H | [10 empty] | PV2 energy total | [25 empty] | 0.1kWh
3062 |  |  |  | Epv2_total L
3063 |  |  |  | Epv3_today H | [10 empty] | PV3 energy today | [25 empty] | 0.1kWh
3064 |  |  |  | Epv3_today L
3065 |  |  |  | Epv3_total H | [10 empty] | PV3 energy total | [25 empty] | 0.1kWh
3066 |  |  |  | Epv3_total L
3067 |  |  |  | Etouser_today H | [10 empty] | Today energy to user | [25 empty] | 0.1kWh |  |  |  |  | Today energy to user
3068 |  |  |  | Etouser_today L
3069 |  |  |  | Etouser_total H | [10 empty] | Total energy to user | [25 empty] | 0.1kWh |  |  |  |  | Total energy to user
3070 |  |  |  | Etouser_total L
3071 |  |  |  | Etogrid_today H | [10 empty] | Today energy to grid | [25 empty] | 0.1kWh |  |  |  |  | Today energy to grid
3072 |  |  |  | Etogrid_today L
3073 |  |  |  | Etogrid_total H | [10 empty] | Total energy to grid | [25 empty] | 0.1kWh |  |  |  |  | Total energy to grid
3074 |  |  |  | Etogrid_total L
3075 |  |  |  | Eload_today H | [10 empty] | Today energy of user load | [25 empty] | 0.1kWh |  |  |  |  | Today energy of user load
3076 |  |  |  | Eload_today L
3077 |  |  |  | Eload_total H | [10 empty] | Total energy of user load | [25 empty] | 0.1kWh |  |  |  |  | Total energy of user load
3078 |  |  |  | Eload_total L
3079 |  |  |  | Reserved
3080 |  |  |  | Reserved
3081 |  |  |  | Reserved
3082 |  |  |  | Reserved
3083 |  |  |  | Reserved
3084 |  |  |  | Reserved
3085 |  |  |  | Reserved
3086 |  |  |  | Reserved
3087 |  |  |  | ISO | [10 empty] | PV ISO value | [25 empty] | 1KΩ
3088 |  |  |  | DCI_R | [10 empty] | R DCI Curr | [25 empty] | 0.1mA
3089 |  |  |  | DCI_S | [10 empty] | S DCI Curr | [25 empty] | 0.1mA
3090 |  |  |  | DCI_T | [10 empty] | T DCI Curr | [25 empty] | 0.1mA
3091 |  |  |  | GFCI | [10 empty] | GFCI Curr | [25 empty] | 1mA
3092 |  |  |  | Reserved
3093 |  |  |  | Temp1 | [10 empty] | Inverter temperature | [25 empty] | 0.1℃
3094 |  |  |  | Temp2 | [10 empty] | The inside IPM in inverter temperature | [25 empty] | 0.1℃
3095 |  |  |  | Temp3 | [10 empty] | Boost temperature | [25 empty] | 0.1℃
3096 |  |  |  | Temp4 | [10 empty] | Reserved | [25 empty] | 0.1℃
3097 |  |  |  | Temp5 | [10 empty] | Commmunication broad temperature | [25 empty] | 0.1℃
3098 |  |  |  | P Bus Voltage | [10 empty] | P Bus inside Voltage | [25 empty] | 0.1V
3099 |  |  |  | N Bus Voltage | [10 empty] | N Bus inside Voltage | [25 empty] | 0.1V
3100 |  |  |  | IPF | [10 empty] | Inverter output PF now | [30 empty] | 0-20000
3101 |  |  |  | RealOPPercent | [10 empty] | Real Output power Percent | [25 empty] | 1% |  |  |  |  | 1~100
3102 |  |  |  | OPFullwatt H | [10 empty] | Output Maxpower Limited | [25 empty] | 0.1W |  |  |  |  | Output Maxpower Limited
3103 |  |  |  | OPFullwatt L
3104 |  |  |  | DeratingMode | [10 empty] | DeratingMode | [30 empty] | 0:no derate; 1:PV;
2:(Reserved) ; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:(Reserved) ; 9:OverBackB yTime;
3105 |  |  |  | Fault code | [10 empty] | Inverter fault code
3106 |  |  |  | Warning code | [10 empty] | Inverter Warning code
3107 |  |  |  | Systemfault word0 | [10 empty] | System fault word0 | [25 empty] | bitfield
3108 |  |  |  | Systemfault word1 | [10 empty] | System fault word1 | [25 empty] | bitfield
3109 |  |  |  | Systemfault word2 | [10 empty] | System fault word2 | [25 empty] | bitfield
3110 |  |  |  | Systemfault word3 | [10 empty] | System fault word3 | [25 empty] | bitfield
3111 |  |  |  | Systemfault word4 | [10 empty] | System fault word4 | [25 empty] | bitfield
3112 |  |  |  | Systemfault word5 | [10 empty] | System fault word5 | [25 empty] | bitfield
3113 |  |  |  | Systemfault word6 | [10 empty] | System fault word6 | [25 empty] | bitfield
3114 |  |  |  | Systemfault word7 | [10 empty] | System fault word7 | [25 empty] | bitfield
3115 |  |  |  | inv start delay time | [10 empty] | inv start delay time | [25 empty] | 1S |  |  |  |  | inv start delay time
3116 |  |  |  | Reserved
3117 |  |  |  | Reserved
3118 |  |  |  | BDC_OnOffState | [10 empty] | BDC connect state | [30 empty] | BDC connect state 0: not detected BDC; 1: BDC detected;
3119 |  |  |  | DryContactState | [10 empty] | Current status of DryContact | [30 empty] | Current status of
DryContact 0: turn off; 1: turn on;
3120 |  |  |  | Reserved
3121 |  |  |  | Reserved
3122 |  |  |  | Reserved
3123 |  |  |  | Reserved
3124 |  |  |  | Reserved
3125 |  |  |  | Edischr_today H | [10 empty] | Today discharge energy | [25 empty] | 0.1kWh |  |  |  |  | Today discharge energy
3126 |  |  |  | Edischr_today L
3127 |  |  |  | Edischr_total H | [10 empty] | Total discharge energy | [25 empty] | 0.1kWh |  |  |  |  | Total discharge energy
3128 |  |  |  | Edischr_total L
3129 |  |  |  | Echr_today H | [10 empty] | Charge energy today | [25 empty] | 0.1kWh |  |  |  |  | Charge energy today
3130 |  |  |  | Echr_today L
3131 |  |  |  | Echr_total H | [10 empty] | Charge energy total | [25 empty] | 0.1kWh |  |  |  |  | Charge energy total
3132 |  |  |  | Echr_total L
3133 |  |  |  | Eacchr_today H | [10 empty] | Today energy of AC charge | [25 empty] | 0.1kWh |  |  |  |  | Today energy of AC charge
3134 |  |  |  | Eacchr_today L
3135 |  |  |  | Eacchr_total H | [10 empty] | Total energy of AC charge | [25 empty] | 0.1kWh |  |  |  |  | Total energy of AC charge
3136 |  |  |  | Eacchr_total L
3137 |  |  |  | Reserved
3138 |  |  |  | Reserved
3139 |  |  |  | Reserved
3140 |  |  |  | Reserved
3141 |  |  |  | Reserved
3142 |  |  |  | Reserved
3143 |  |  |  | Reserved
3144 |  |  |  | Reserved
3145 |  |  |  | EPS Fac | [10 empty] | UPS frequency | [25 empty] | 0.01Hz
3146 |  |  |  | EPS Vac1 | [10 empty] | UPS phase R output voltage | [25 empty] | 0.1V
3147 |  |  |  | EPS Iac1 | [10 empty] | UPS phase R output current | [25 empty] | 0.1A
3148 |  |  |  | EPS Pac1 H | [10 empty] | UPS phase R output power | [25 empty] | 0.1VA
3149 |  |  |  | EPS Pac1 L
3150 |  |  |  | EPS Vac2 | [10 empty] | UPS phase S output voltage | [25 empty] | 0.1V
3151 |  |  |  | EPS Iac2 | [10 empty] | UPS phase S output current | [25 empty] | 0.1A
3152 |  |  |  | EPS Pac2 H | [10 empty] | UPS phase S output power | [25 empty] | 0.1VA
3153 |  |  |  | EPS Pac2 L
3154 |  |  |  | EPS Vac3 | [10 empty] | UPS phase T output voltage | [25 empty] | 0.1V
3155 |  |  |  | EPS Iac3 | [10 empty] | UPS phase T output current | [25 empty] | 0.1A
3156 |  |  |  | EPS Pac3 H | [10 empty] | UPS phase T output power | [25 empty] | 0.1VA
3157 |  |  |  | EPS Pac3 L
3158 |  |  |  | EPS Pac H | [10 empty] | UPS output power | [25 empty] | 0.1VA
3159 |  |  |  | EPS Pac L
3160 |  |  |  | Loadpercent | [10 empty] | Load percent of UPS ouput | [25 empty] | 0.1%
3161 |  |  |  | PF | [10 empty] | Power factor | [25 empty] | 0.1
3162 |  |  |  | DCV | [10 empty] | DC voltage | [25 empty] | 1mV
3163 |  |  |  | Reserved
3164 |  |  |  | Reserved
3165 |  |  |  | Reserved
3166 |  |  |  | SysState_Mode | [10 empty] | System work State and mode 高 8 位表示模式； 0：No charge and discharge； 1：charge； 2：Discharge； 低 8 位表示状态； 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus; | [30 empty] | BDC1
3167 |  |  |  | FaultCode | [10 empty] | Storge device fault code
3168 |  |  |  | WarnCode | [10 empty] | Storge device warning code
3169 |  |  |  | Vbat | [10 empty] | Battery voltage | [25 empty] | 0.01V
3170 |  |  |  | Ibat | [10 empty] | Battery current | [25 empty] | 0.1A
3171 |  |  |  | SOC | [10 empty] | State of charge Capacity | [25 empty] | 1%
3172 |  |  |  | Vbus1 | [10 empty] | BUS1 voltage | [25 empty] | 0.1V
3173 |  |  |  | Vbus2 | [10 empty] | BUS2 voltage | [25 empty] | 0.1V
3174 |  |  |  | Ibb | [10 empty] | BUCK-BOOST Current | [25 empty] | 0.1A
3175 |  |  |  | Illc | [10 empty] | LLC Current | [25 empty] | 0.1A
3176 |  |  |  | TempA | [10 empty] | Temperture A | [25 empty] | 0.1℃
3177 |  |  |  | TempB | [10 empty] | Temperture B | [25 empty] | 0.1℃
3178 |  |  |  | Pdischr H | [10 empty] | Discharge power | [25 empty] | 0.1W
3179 |  |  |  | Pdischr L
3180 |  |  |  | Pchr H | [10 empty] | Charge power | [25 empty] | 0.1W
3181 |  |  |  | Pchr L
3182 |  |  |  | Edischr_total H | [10 empty] | Discharge total energy of storge device | [25 empty] | 0.1kWh
3183 |  |  |  | Edischr_total L
3184 |  |  |  | Echr_total H | [10 empty] | Charge total energy of storge device | [25 empty] | 0.1kWh
3185 |  |  |  | Echr_total L
3186 |  |  |  | AutoProofreadC MD | [10 empty] | ATE mode adjust cmd
3187 |  |  |  | Reserved
3188 |  |  |  | Reserved
3189 |  |  |  | SysState_Mode | [10 empty] | System work State and mode 高 8 位表示模式； 0：No charge and discharge； 1：charge； 2：Discharge； 低 8 位表示状态； 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus；
3190 |  |  |  | FaultCode | [10 empty] | Storge device fault code | [30 empty] | BDC2
3191 |  |  |  | WarnCode | [10 empty] | Storge device warning code
3192 |  |  |  | Vbat | [10 empty] | Battery voltage | [25 empty] | 0.01V
3193 |  |  |  | Ibat | [10 empty] | Battery current | [25 empty] | 0.1A
3194 |  |  |  | SOC | [10 empty] | State of charge Capacity | [25 empty] | 1%
3195 |  |  |  | Vbus1 | [10 empty] | BUS1 voltage | [25 empty] | 0.1V
3196 |  |  |  | Vbus2 | [10 empty] | BUS2 voltage | [25 empty] | 0.1V
3197 |  |  |  | Ibb | [10 empty] | BUCK-BOOST Current | [25 empty] | 0.1A
3198 |  |  |  | Illc | [10 empty] | LLC Current | [25 empty] | 0.1A
3199 |  |  |  | TempA | [10 empty] | Temperture A | [25 empty] | 0.1℃
3200 |  |  |  | TempB | [10 empty] | Temperture B | [25 empty] | 0.1℃
3201 |  |  |  | Pdischr H | [10 empty] | Discharge power | [25 empty] | 0.1W
3202 |  |  |  | Pdischr L
3203 |  |  |  | Pchr H | [10 empty] | Charge power | [25 empty] | 0.1W
3204 |  |  |  | Pchr L
3205 |  |  |  | Edischr_total H | [10 empty] | Discharge total energy of storge device | [25 empty] | 0.1kWh
3206 |  |  |  | Edischr_total L
3207 |  |  |  | Echr_total H | [10 empty] | Charge total energy of storge device | [25 empty] | 0.1kWh
3208 |  |  |  | Echr_total L
3209 |  |  |  | AutoProofreadC MD | [10 empty] | ATE mode adjust cmd
3210 |  |  |  | Reserved
3211 |  |  |  | Reserved
3212 |  |  |  | BMS_Status | [10 empty] | Status from BMS
3213 |  |  |  | BMS_Error | [10 empty] | Error information from BMS
3214 |  |  |  | BMS_WarnInfo | [10 empty] | Warning information from BMS
3215 |  |  |  | BMS_SOC | [10 empty] | SOC from BMS
3216 |  |  |  | BMS_BatteryVol t | [10 empty] | Battery voltage from BMS
3217 |  |  |  | BMS_BatteryCur r | [10 empty] | Battery current from BMS
3218 |  |  |  | BMS_BatteryTe mp | [10 empty] | Battery temperature from BMS
3219 |  |  |  | BMS_MaxCurr | [10 empty] | Max. charge/discharge current from BMS (pylon)
3220 |  |  |  | BMS_DeltaVolt | [10 empty] | Delta V from BMS
3221 |  |  |  | BMS_CycleCnt | [10 empty] | Cycle Count from BMS
3222 |  |  |  | BMS_SOH | [10 empty] | SOH from BMS
3223 |  |  |  | BMS_ConstantV olt | [10 empty] | CV voltage from BMS
3224 |  |  |  | BMS_BMSInfo | [10 empty] | BMSInformation from BMS
3225 |  |  |  | BMS_PackInfo | [10 empty] | Pack Information from BMS
3226 |  |  |  | BMS_UsingCap | [10 empty] | Using Cap from BMS
3227 |  |  |  | BMS_FW
3228 |  |  |  | BMS_MCUVersi on | [10 empty] | MCU Software version from BMS
3229 |  |  |  | BMSCommType | [10 empty] | BMS Communication Type | [30 empty] | BMS Communicat ion Type 0: RS485; 1: CAN;
3230 ~ 3249 |  |  |  | Reserved
&*1: Inverter fault code Bit:
|  | Fault type value | [11 empty] | Means(The message showed on the inverter when the inverter has fault)
|  | 1~23 | [11 empty] | " Error: 99+x ",
|  | 24 | [11 empty] | "Auto Test Failed",
|  | 25 | [11 empty] | "No AC Connection",
|  | 26 | [11 empty] | "PV Isolation Low",
|  | 27 | [11 empty] | " Residual I High",
|  | 28 | [11 empty] | " Output High DCI",
|  | 29 | [11 empty] | " PV Voltage High",
|  | 30 | [11 empty] | " AC V Outrange ",
31 | [11 empty] | " AC F Outrange ",
32 | [11 empty] | " Module Hot "
&*2: The value is 0.1V when the fault is the voltage, is 0.01Hz when the fault is the frequency; &*3:
|  |  |  | High byte value | [6 empty] | Means | [9 empty] | low byte value | [6 empty] | Means
|  |  |  | 0 | [6 empty] | Auto test stop | [9 empty] | 0 | [6 empty] | No test
|  |  |  | 1 | [6 empty] | Auto test starting | [9 empty] | 1 | [6 empty] | Testing grid volt high pro
|  |  |  | 2 | [6 empty] | Auto testing | [9 empty] | 2 | [6 empty] | Testing grid volt low pro
[21 empty] | 3 | [6 empty] | Testing grid frequency high pro
[21 empty] | 4 | [6 empty] | Testing grid frequency low pro
&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time counter, when it reach cTestStepStop, this step test will stop and fail. &*5: Inverter Model: A , could be show: “A1 B0 D0 T0 PF U1 M5 S1” or “1000F151” Ax=(A&0XF00000000)>>28 Bx=(A&0XF0000000)>>24 Dx=(A&0XF000000)>>20 Tx=(A&0XF00000)>>16 Px=(A&0x00F000)>>12 Ux=(A&0x000F00)>>8 Mx=(A&0x0000F0)>>4 Sx=(A&0x00000F) &*6: DTC(Device type code)
[8 empty] | Code No. |  |  |  |  | Device type | [7 empty] | Note
[8 empty] | 001xx |  |  |  |  | Inverter | [7 empty] | 1 tracker and 1phase Grid connect PV inverter TL
[8 empty] | 002xx |  |  |  |  | Inverter | [7 empty] | 2 tracker and 1phase Grid connect PV inverter TL
[8 empty] | 003xx |  |  |  |  | Inverter | [7 empty] | 1 tracker and 1phase Grid connect PV inverter HF
[8 empty] | 004xx |  |  |  |  | Inverter | [7 empty] | 2 tracker and 1phase Grid connect PV inverter HF
[8 empty] | 005xx |  |  |  |  | Inverter | [7 empty] | 1 tracker and 1phase Grid connect PV inverter LF
[8 empty] | 006xx |  |  |  |  | Inverter | [7 empty] | 2 tracker and 1phase Grid connect PV inverter LF
[8 empty] | 007xx |  |  |  |  | Inverter | [7 empty] | 1 tracker and 3phase Grid connect PV inverter TL
[8 empty] | 008xx |  |  |  |  | Inverter | [7 empty] | 2 tracker and 3phase Grid connect PV inverter TL
[8 empty] | 009xx |  |  |  |  | Inverter | [7 empty] | 1 tracker and 3phase Grid connect PV inverter LF
[8 empty] | 010xx |  |  |  |  | Inverter | [7 empty] | 2 tracker and 3phase Grid connect PV inverter LF
……
[8 empty] | 10001 |  |  |  |  | Data logger | [7 empty] | RF-ShineVersion
[8 empty] | 10002 |  |  |  |  | Data logger | [7 empty] | Web-ShinePano
[8 empty] | 10003 |  |  |  |  | Data logger | [7 empty] | Web-ShineWebBox
[8 empty] | 10004 |  |  |  |  | Data logger | [7 empty] | WL-WIFI Module
……
[8 empty] | 11001 |  |  |  |  | Confluence box | [7 empty] | Confluence box 1
……
&*7: Grid network power control command password: Inverter is in lock state after power on; change the power control by network command should unlock inverter first; default pw is XXXXXX; Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after unlocked; Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138; Lock: send 0 or 2 to 3-135;
&*8: Inverter fault code and warning code
Fault code | [25 empty] | Warning code
0x00000001 | [8 empty] | \ | [16 empty] | 0x0001 | [6 empty] | Fan warning
0x00000002 | [8 empty] | Communication error | [16 empty] | 0x0002 | [6 empty] | String communication abnormal
0x00000004 | [8 empty] | \ | [16 empty] | 0x0004 | [6 empty] | StrPIDconfig Warning
0x00000008 | [8 empty] | StrReverse or StrShort fault | [16 empty] | 0x0008 | [6 empty] | \
0x00000010 | [8 empty] | Model Init fault | [16 empty] | 0x0010 | [6 empty] | DSP and COM firmware unmatch
0x00000020 | [8 empty] | Grid Volt Sample diffirent | [16 empty] | 0x0020 | [6 empty] | \
0x00000040 | [8 empty] | ISO Sample diffirent | [16 empty] | 0x0040 | [6 empty] | SPD abnormal
0x00000080 | [8 empty] | GFCI Sample diffirent | [16 empty] | 0x0080 | [6 empty] | GND and N connect abnormal
0x00000100 | [8 empty] | \ | [16 empty] | 0x0100 | [6 empty] | PV1 or PV2 circuit short
0x00000200 | [8 empty] | \ | [16 empty] | 0x0200 | [6 empty] | PV1 or PV2 boost driver broken
0x00000400 | [8 empty] | \ | [16 empty] | 0x0400 | [6 empty] | \
0x00000800 | [8 empty] | \ | [16 empty] | 0x0800 | [6 empty] | \
0x00001000 | [8 empty] | AFCI Fault | [16 empty] | 0x1000 | [6 empty] | \
0x00002000 | [8 empty] | \ | [16 empty] | 0x2000 | [6 empty] | \
0x00004000 | [8 empty] | AFCI Module fault | [16 empty] | 0x4000 | [6 empty] | \
0x00008000 | [8 empty] | \ | [16 empty] | 0x8000 | [6 empty] | \
0x00010000 | [8 empty] | \
0x00020000 | [8 empty] | Relay check fault
0x00040000 | [8 empty] | \
0x00080000 | [8 empty] | \
0x00100000 | [8 empty] | \
0x00200000 | [8 empty] | Communication error
0x00400000 | [8 empty] | Bus Voltage error
0x00800000 | [8 empty] | AutoTest fail
0x01000000 | [8 empty] | No Utility
0x02000000 | [8 empty] | PV Isolation Low
0x04000000 | [8 empty] | Residual I High
0x08000000 | [8 empty] | Output High DCI
0x10000000 | [8 empty] | PV Voltage high
0x20000000 | [8 empty] | AC V Outrange
0x40000000 | [8 empty] | AC F Outrange
0x80000000 | [8 empty] | TempratureHigh
&*9 Warning Value
[7 empty] | Warning Value 1 | [12 empty] | Warning Value 2 | [16 empty] | Warning Value 3
0x0001 | [6 empty] | String1abnormal | [12 empty] | PV1ShortCircuit | [16 empty] | AC SPD abnormal
0x0002 | [6 empty] | String2abnormal | [12 empty] | PV2ShortCircuit | [16 empty] | DC SPD abnormal
0x0004 | [6 empty] | String3abnormal | [12 empty] | PV3ShortCircuit
0x0008 | [6 empty] | String4abnormal | [12 empty] | PV4ShortCircuit
0x0010 | [6 empty] | String5abnormal | [12 empty] | PV5ShortCircuit
0x0020 | [6 empty] | String6abnormal | [12 empty] | PV6ShortCircuit
0x0040 | [6 empty] | String7abnormal | [12 empty] | PV7ShortCircuit
0x0080 | [6 empty] | String8abnormal | [12 empty] | PV8ShortCircuit
0x0100 | [6 empty] | String9abnormal | [12 empty] | BT1DriverFault
0x0200 | [6 empty] | String10abnormal | [12 empty] | BT2DriverFault
0x0400 | [6 empty] | String11abnormal | [12 empty] | BT3DriverFault
0x0800 | [6 empty] | String12abnormal | [12 empty] | BT4DriverFault
0x1000 | [6 empty] | String13abnormal | [12 empty] | BT5DriverFault
0x2000 | [6 empty] | String14abnormal | [12 empty] | BT6DriverFault
0x4000 | [6 empty] | String15abnormal | [12 empty] | BT7DriverFault
0x8000 | [6 empty] | String16abnormal | [12 empty] | BT8DriverFault
&*11: Inverter Model: A , could be show: “S0A D01 B01 T06 P0F U01 M03E8” or “0A0101060F0103E8” Sx=(A&0XFF00000000000000)>>56 Dx=(A&0X00FF000000000000)>>48 Bx=(A&0X0000FF0000000000)>>40 Tx=(A&0X000000FF00000000)>>32 Px=(A&0x00000000FF000000)>>24 Ux=(A&0x0000000000FF0000)>>16 Mx=(A&0x000000000000FFFF)
HybridAbnoram/Fault/warning bit definition (Abnormal:record event for debug,continueworking;fault:record event and show for
debug,stopworking;Warning:record event and show,continue working)
Word definition | [16 empty] | Bit definition | [17 empty] | comment
System fault word0 | [9 empty] | Byte0 | [6 empty] | MasterForceINVFault | [13 empty] | 0 |  |  |  | M3 on/off control
[17 empty] | MasterForceSPFault | [13 empty] | 1
[17 empty] | BusVoltHigh_TZ | [13 empty] | 2 |  |  |  | restart PWM
[17 empty] | BusVoltHigh_ISR | [13 empty] | 3 |  |  |  | restartPWM
[17 empty] | reserved | [13 empty] | 4
[17 empty] | reserved | [13 empty] | 5
[17 empty] | reserved | [13 empty] | 6
[17 empty] | reserved | [13 empty] | 7
[10 empty] | Byte1 | [6 empty] | GridZClossFault | [13 empty] | 8 |  |  |  | Grid side abnormal
[17 empty] | reserved | [13 empty] | 9
[17 empty] | reserved | [13 empty] | 10
[17 empty] | GFCIHigh | [13 empty] | 11
[17 empty] | GridR_VFault | [13 empty] | 12
[17 empty] | GridS_VFault | [13 empty] | 13
[17 empty] | GridT_VFault | [13 empty] | 14
[17 empty] | GridFFault | [13 empty] | 15
System fault word1 | [9 empty] | Byte2 | [6 empty] | RelayFault | [13 empty] | 0 |  |  |  | Grid side abnormal
[17 empty] | GFCIDamage | [13 empty] | 1
[17 empty] | GridR_VLowFault | [13 empty] | 2
[17 empty] | GridR_VHighFault | [13 empty] | 3
[17 empty] | GridS_VLowFault | [13 empty] | 4
[17 empty] | GridS_VHighFault | [13 empty] | 5
[17 empty] | GridT_VLowFault | [13 empty] | 6
[17 empty] | GridT_VHighFault | [13 empty] | 7
[10 empty] | Byte3 | [6 empty] | INVCurrOCP_ISR | [13 empty] | 8 |  |  |  | Grid side abnormal
[17 empty] | INVCurrOCP_TZ | [13 empty] | 9
[17 empty] | DCIHigh | [13 empty] | 10
[17 empty] | reserved | [13 empty] | 11
[17 empty] | INVR_CurrOCP_Rms | [13 empty] | 12
[17 empty] | INVS_CurrOCP_Rms | [13 empty] | 13
[17 empty] | INVT_CurrOCP_Rms | [13 empty] | 14
[17 empty] | NoUtility | [13 empty] | 15
System fault word2 | [9 empty] | Byte4 | [6 empty] | GridFLowFault | [13 empty] | 0 |  |  |  | Grid side abnormal
[17 empty] | GridFHighFault | [13 empty] | 1
[17 empty] | GridVolt_Unbalance_Fault | [13 empty] | 2
[17 empty] | AC_PLL_Fault | [13 empty] | 3
[17 empty] | OverLoadFault | [13 empty] | 4
[17 empty] | reserved | [13 empty] | 5
[17 empty] | reserved | [13 empty] | 6
[17 empty] | reserved | [13 empty] | 7
[10 empty] | Byte5 | [6 empty] | EPS_LineVoltR_Loss | [13 empty] | 8 |  |  |  | EPS side abnormal
[17 empty] | EPS_LineVoltS_Loss | [13 empty] | 9
[17 empty] | EPS_LineVoltT_Loss | [13 empty] | 10
[17 empty] | reserved | [13 empty] | 11
[17 empty] | reserved | [13 empty] | 12
[17 empty] | reserved | [13 empty] | 13
[17 empty] | reserved | [13 empty] | 14
[17 empty] | reserved | [13 empty] | 15
System fault word3 | [9 empty] | Byte6 | [6 empty] | BatTerminalReversed | [13 empty] | 0 |  |  |  | BAT Side abnormal
[17 empty] | BatTerminalOpen | [13 empty] | 1
BMS Battery Open
[17 empty] | BatteryVoltageLow | [13 empty] | 2
[17 empty] | BatteryVoltageHigh | [13 empty] | 3
[17 empty] | reserved | [13 empty] | 4
[17 empty] | reserved | [13 empty] | 5
[17 empty] | reserved | [13 empty] | 6
[17 empty] | reserved | [13 empty] | 7
[10 empty] | Byte7 | [6 empty] | reserved | [13 empty] | 8 |  |  |  | BAT Side abnormal
[17 empty] | reserved | [13 empty] | 9
[17 empty] | reserved | [13 empty] | 10
[17 empty] | reserved | [13 empty] | 11
[17 empty] | reserved | [13 empty] | 12
[17 empty] | reserved | [13 empty] | 13
[17 empty] | reserved | [13 empty] | 14
[17 empty] | reserved | [13 empty] | 15
System fault word4 | [9 empty] | Byte8 | [6 empty] | reserved | [13 empty] | 0 |  |  |  | PV Side Abnormal
[17 empty] | reserved | [13 empty] | 1
[17 empty] | reserved | [13 empty] | 2
[17 empty] | reserved | [13 empty] | 3
[17 empty] | reserved | [13 empty] | 4
[17 empty] | PV1_VoltLowWarn | [13 empty] | 5
[17 empty] | PV2-VoltLowWarn | [13 empty] | 6
[17 empty] | reserved | [13 empty] | 7
[10 empty] | Byte9 | [20 empty] | 8 |  |  |  | PV Side Abnormal
9
10
[17 empty] | reserved | [13 empty] | 11
[17 empty] | reserved | [13 empty] | 12
[17 empty] | reserved | [13 empty] | 13
[17 empty] | reserved | [13 empty] | 14
[17 empty] | reserved | [13 empty] | 15
System fault word5 | [9 empty] | Byte10 | [6 empty] | NEDetectFault | [13 empty] | 0 |  |  |  | Sytem fault
[17 empty] | PVISOFault | [13 empty] | 1
[17 empty] | reserved | [13 empty] | 2
[17 empty] | BusVoltHighFault_ISR | [13 empty] | 3
[17 empty] | BusSampleFault | [13 empty] | 4
[17 empty] | UHCTFault | [13 empty] | 5
[17 empty] | AComFault | [13 empty] | 6
[17 empty] | BComFault | [13 empty] | 7
[10 empty] | Byte11 | [6 empty] | BusVoltHighFault_TZ | [13 empty] | 8 |  |  |  | Sytem fault
[17 empty] | AuotTestFault | [13 empty] | 9
[17 empty] | DCIHigh | [13 empty] | 10
[17 empty] | NTCOpenFault | [13 empty] | 11
[17 empty] | reserved | [13 empty] | 12
[17 empty] | BBHeatsink_TempOver | [13 empty] | 13
[17 empty] | BBOCP_FaultISR | [13 empty] | 14
[17 empty] | BBOCP_FaultTZ | [13 empty] | 15
System fault word6 | [9 empty] | Byte12 | [6 empty] | PV1_VoltHighFault | [13 empty] | 0 |  |  |  | Sytem fault
[17 empty] | PV2_VoltHighFault | [13 empty] | 1
[17 empty] | BTHeatsink_Overtemp | [13 empty] | 2
[17 empty] | INVHeatsink_Overtemp | [13 empty] | 3
[17 empty] | reserved | [13 empty] | 4
[17 empty] | reserved | [13 empty] | 5
[17 empty] | reserved | [13 empty] | 6
[17 empty] | reserved | [13 empty] | 7
[10 empty] | Byte13 | [6 empty] | BoostDriver1Warn | [13 empty] | 8 |  |  |  | System warning
[17 empty] | BoostDriver2Warn | [13 empty] | 9
[17 empty] | WARN104 | [13 empty] | 10
[17 empty] | PV1_ShortFault | [13 empty] | 11
[17 empty] | PV2_ShortFault | [13 empty] | 12
[17 empty] | Meter Comm Loss | [13 empty] | 13
[17 empty] | PairingTimeOut | [13 empty] | 14
[17 empty] | CT LN Reversed | [13 empty] | 15
System fault word6 | [9 empty] | Byte14 | [6 empty] | BMS COM Fault | [13 empty] | 0
[17 empty] | BMS Error: xxx | [13 empty] | 1
[17 empty] | Battery reversed | [13 empty] | 2
[17 empty] | BAT NTC Open | [13 empty] | 3
[17 empty] | SS Timeout | [13 empty] | 4
[17 empty] | Bat voltage low | [13 empty] | 5
[17 empty] | Bat T Outrange | [13 empty] | 6
[17 empty] | BATOutput_Overload | [13 empty] | 7
[10 empty] | Byte15 | [6 empty] | reserved | [13 empty] | 8
[17 empty] | reserved | [13 empty] | 9
[17 empty] | reserved | [13 empty] | 10
[17 empty] | reserved | [13 empty] | 11
[17 empty] | reserved | [13 empty] | 12
[17 empty] | reserved | [13 empty] | 13
[17 empty] | reserved | [13 empty] | 14
[17 empty] | reserved | [13 empty] | 15
System fault word7 | [16 empty] | reserved
5 Set address
Refer to the Inverter user manual. Always is : Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.
6 Notice
1) It can drive mostly 32 pv inverters for one rs485 comport. 2) There are only read input and hold registers commands even the newest version. 3) App user could only care the input register. 4) App user could not care the holding registers. 5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;