## Table 1
Growatt PV Inverter Modbus RS485 RTU Protocol V3.14 2016-09-27 Growatt New Energy CO.,LTD
No. |  |  | Version | [5 empty] | Date |  | Notice | [8 empty] | Signature
1 |  |  | V1.00 | [5 empty] | 2011-08-30 |  | The first version | [8 empty] | Paco
2 |  |  | V1.10 | [5 empty] | 2011-10-20 |  | X | [8 empty] | Lin
3 |  |  | V2.01 | [5 empty] | 2011-11-02 |  | Update Modbus mostly protocol | [8 empty] | Xin.Chen
… |  |  | … | [5 empty] | … |  | … | [8 empty] | …
19 |  |  | V3.00 | [5 empty] | 2012-08-15 |  | add 3-113~115, 4-48~63, 4-450~575, | [8 empty] | Jumi
20 |  |  | V3.01 | [5 empty] | 2012-11-22 |  | Add many CEI registers | [8 empty] | Jumi
21 |  |  | V3.02 | [5 empty] | 2013-01-26 |  | Add some reserved registers | [8 empty] | Jumi
22 |  |  | V3.03 | [5 empty] | 2013-01-30 |  | Change 485 Time out limit | [8 empty] | Jumi
23 |  |  | V3.04 | [5 empty] | 2013-02-28 |  | Chang holding 80 and 150 | [8 empty] | Jumi
24 |  |  | V3.05 | [5 empty] | 2014-12-30 |  | add 3-180~191
25 |  |  | V3.06 | [5 empty] | 2015-03-09 |  | Add address to dis/enable N to GND detect | [8 empty] | Jason
26 |  |  | V3.07 | [5 empty] | 2015-05-22 |  | Add hold 165 and 166 for CEI delay time
27 |  |  | V3.08 | [5 empty] | 2015-07-24 |  | Add holding 194
28 |  |  | V3.09 | [5 empty] | 2015-09-28 |  | Add holding 195~200 for network | [8 empty] | Zhenyuan.li
29 |  |  | V3.10 | [5 empty] | 2015-12-17 |  | Add Input 70~89 for string monitor | [8 empty] | May
30 |  |  | V3.11 | [5 empty] | 2016-04-01 |  | Add holding 87~89 and input 115~119 for PID information | [8 empty] | Hui.zhao
31 |  |  | V3.12 | [5 empty] | 2016-05-19 |  | Add InputReg 120-127 to get PV3 Information | [8 empty] | Jason
32 |  |  | V3.13 | [5 empty] | 2016-08-04 |  | Add holding 167-170 for softstartflag,QPercentMax,DRMS and PowerVoltFuncEn Enable Add Inputreg128~129 for transfer fault code as &*8 | [8 empty] | Pan.xie
33 |  |  | V3.14 | [5 empty] | 2016-09-27 |  | Add holding 171-175 for input parameters setting | [8 empty] | Shuang.he
V2.01 2011-11-2: 1, Update the four register map tables 2, Add maximum data length define 3,Change the parity type of RS232 V2.02 2011-11-4: 1, Add the flash command V2.03 2012-03-01 1, Combine the read and write register map table 2, Update the register map of 4.1 and 4.2 by blue marked; V2.04 2012-03-05 1， Add system time read and write cmd V2.05 2012-03-06 1, Add Grid V/F Outrange protect time read and write cmd V2.06 2012-03-21 1, Add Auto test start cmd; 2, Move Manufacturer info from 13 to 60. V2.07 2012-04-19 1, Add holding registers: 13~15, 40~45, 68~71, 73, 74; V2.08 2012-04-28 1, Shift the all reg address, start at 0x0000; V2.09 2012-05-09 1, Add 4-45 PF register, to read and adjust inverter output PF; 2,Add3-90~99 registers, to set the PF limit line,(this function is resaved for internal); V2.10 2012-05-10 1, Add 4-180~429 registers, for the 50 records of the inverter error info; V2.11 2012-05-29 1, Add 3-1,100~107 registers, for the frequency – load limit rate and the PF check adjust values; 2, Change the Input Pac registers’s unit, from watt to power (W--VA) ; V2.12 2012-06-14 1, Change 3-3 register define; 2, Change 3-90~99 registers, change the PF line define; 3, Add 3-135~138 grid spec network command password registers, V2.13 2012-06-27 1, chg 3-99 register, add 3-108~112 V2.14 2012-07-17 1, add 3-74 euro inverter spec select cmd, 3-98 CEI freq. test cmd; 2,add 3-80~89, 4-80~89 resaved registers, for the outsourcing device updating; V2.15 V2.16 2012-07-31 1, add 4-48~63 pv energy , reactive power and energy registers; V3.00 2012-08-15 1, add 3-113~115 registers, for CEI021 model set; 2, add 4-48~63 registers, for PV energy and reactive ac energy; 3, add 4-450~575 registers, for history energy records; V3.01 2012-11-22:
1,add 3-75 232T485Enable; 2,add 3-116~119, 6KwSystem, FrequencyDeratingEnable, QlockOutpower, RestartDelayTime 3,add 4-47 DeratingMode; 4,add others; V3.02 2013-01-26: 1,add power control registers in holding map; 2,add debug resaved registers in input map; 3,change 24 hours energy means; 4, notice the minimum period of the CMD; V3.03 2013-01-30: 1,change 485 time out limit; V3.04 2013-02-28: 1,change holding 80 register to ODM factory Info; 2,add holding 81 register for the point of over-frequency derate load; 2,add holding 150 register to start Fan check; V3.05 2014-12-30: 1,add holding 180~182 register for the Internet IP; 2,add holding 184~191 register for the MTL-US 6K protect level 3; 3,add input 69 register for warning value of main CPU V3.06 2015-03-09: 1, add holding 192 register to enable or disable N to GND detect 2, add holding 193 register to enable appointed Spec setting // 2015-03-19 V3.07 2015-05-22: 1, Add holding 165 register as delay time for Q(V) activation 2, Add holding 166 register as delay time for over-frequency load derating activation V3.08 2015-07-24： 1,Add holding 194 register to enable or disable non-standard AC voltage range V3.09 2015-09-28： 1,add holding 195~196 register for the server IP; 2,add holding 197 register for the send data Interval; 3,add holding 198~200 register for Datalogger Check Code; V3.10 2015-12-17： 1, Add Input 70~89 for string monitor; V3.11 2016-04-01： 1, Add holding 87~89 and input 115~119 for PID information; V3.12 2016-5-19： Add InputReg 120-127，For getting PV3 voltage/current/power/E_Today/E_total information V3.13 2016-8-9： 1, Add holding 167-169 for Australia Spe；167：load softstart enable 168: Qmax for Q(V) curve 169: DRMS Enable 170: PowerVoltFuncEn 2, Add Inputreg128~129 for transfer faultcode as &*8
V3.14 2016-9-27: Add holding 171-175 for input parameters setting. 171: INVWorkModeSetting 172: PV1VoltSet 173:PV2VoltSet 174:BT1CurrRefSet 175: BT2CurrRefSet 2016-12-19: Add holding 131 register for power restart slope setting Add holding 132 register for load derating of over AC voltage start point setting Add holding 149 register for over AC voltage load derating slope setting Add holding 176 register for Delay time for power recovering when ac voltage getting normal
1 Data format 6 2 Command Format 6 3 Device Message Transmission Mode / Framing 9 4 Register map 9 5 Set address 31 6 Notice 32
1 Data format Valid slave device addresses are in the range of 0 – 247 decimal. The individual slave devices are assigned addresses in the range of 1 – 247. 0 is the broadcast address It is 16bits (two bytes) unsigned integer for each holding and input register; 2 Command Format Function 3 Read holding register Response Error: 11 0x80¦0x03 Errornum CRC (Errornum as a byte)
Function 4 Read input register Response Error: 11 0x80¦0x04 Errornum CRC (Errornum as a byte) Function 6 Preset single register
Response Error: 11 0x80¦0x06 Errornum CRC (Errornum as a byte) Function 16 Preset multiple register Response Error: 11 0x80¦0x10 Errornum CRC (Errornum as a byte)
3 Device Message Transmission Mode / Framing RTU Mode When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream. The format for each byte in RTU mode is: Coding System: 8–bit binary, hexadecimal 0–9, A–F Two hexadecimal characters contained in each 8–bit field of the message
Bits per Byte: |  |  |  | 1 start bit 8 data bits, least significant bit sent first None parity 1 stop bit Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is: Baud Rate: 9600 bps Minimum CMD period (RS485 Time out): 850ms. Wait for minimum 850ms to send a new CMD after last CMD. Suggestion is 1s; Maximum Data Length Define: Maximum read data length is 45 words in read command; Maximum update data length is 45 words in preset command; Read or update registers NO. should in the range of times of 45, eg: 1~45 or 96~123 are OK, but 40~60 is not OK; Note: Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers; 4 Register map It is 16bits (two bytes) unsigned integer for each holding and input register; 4.1 Holding Reg
Regis ter NO. |  | Variable Name | [5 empty] | Description |  |  |  |  | C us to m er W rit e | Value |  |  | Unit |  | Initial value |  | Note
0 |  | OnOff | [5 empty] | The Inverter On/Off state and the auto start state, The low byte is the on/off(1/0), the high byte is the auto start state or not(1/0). |  |  |  |  | W | 0x0000; 0x0001; 0x0100; 0x0101; |  |  |  |  | 0x010 1; |  | Auto start means the auto power AC when next power on inverter.
1 |  | SPIenable | [5 empty] | SPI(system protection interface) function enable |  |  |  |  | W | 0or1, | [6 empty] | Now only for CEI021
2 |  | PF CMD memory state | [5 empty] | Set the following 3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. |  |  |  |  | W | 0or1, |  |  |  |  | 0 |  | Means these settings will be acting or not when next power on
3 |  | Active Rate |  |  |  | P |  | Read Inverter max output active power percent |  |  |  |  | W | 0-100 |  |  | perce nt |  | 100
4 |  | Reactive Rate |  |  |  | P |  | Read Inverter max output reactive power percent |  |  |  |  | W | 0-100 |  |  | perce nt
5 |  | Power factor | [5 empty] | Read Inverter output power factor’s 10000 times |  |  |  |  | W | 0-20000， 0-10000 is underexcite c, other is overexcited |  |  |  |  | 10000
6 |  | Pmax H | [5 empty] | Normal (high) |  | power | [6 empty] | 0.1VA
7 |  | Pmax L | [5 empty] | Normal (low) |  | power | [6 empty] | 0.1VA
8 |  | Vnormal | [5 empty] | Normal work PV voltage | [8 empty] | 0.1V
9 |  | Fw version H | [5 empty] | Firmware version (high) | [8 empty] | ASCII
10 |  | Fw version M | [5 empty] | Firmware version (middle)
11 |  | Fw version L | [5 empty] | Firmware version (low)
12 |  | Fw version2 H | [5 empty] | Control Firmware version (high) | [8 empty] | ASCII
13 |  | Fw version2 M | [5 empty] | Control Firmware version (middle)
14 |  | Fw version2 L | [5 empty] | Control Firmware version (low)
15 |  | LCD language | [5 empty] | LCD language |  |  |  |  | W | 0-4,5
16 |  | LCD Contrast | [5 empty] | LCD Contrast |  |  |  |  | W
17 |  | Vpv start | [5 empty] | Input start voltage |  |  |  |  | W |  |  |  | 0.1V
18 |  | Time start | [5 empty] | Start time |  |  |  |  | W |  |  |  | 1S
19 |  | Vac low | [5 empty] | Grid voltage low limit protect |  |  |  |  | W |  |  |  | 0.1V
20 |  | Vac high | [5 empty] | Grid voltage high limit protect |  |  |  |  | W |  |  |  | 0.1V
21 |  | Fac low | [5 empty] | Grid frequency low limit protect |  |  |  |  | W |  |  |  | 0.01 Hz
22 |  | Fac high | [5 empty] | Grid high frequency limit protect |  |  |  |  | W |  |  |  | 0.01 Hz
23 |  | Serial NO. 5 | [5 empty] | Serial number 5 | [8 empty] | ASCII
24 |  | Serial No. 4 | [5 empty] | Serial number 4
25 |  | Serial No. 3 | [5 empty] | Serial number 3
26 |  | Serial No. 2 | [5 empty] | Serial number 2
27 |  | Serial No. 1 | [5 empty] | Serial number 1
28 |  | Moudle H | [5 empty] | Inverter Moudle (high) | [5 empty] | &*5
29 |  | Moudle L | [5 empty] | Inverter Moudle (low)
30 |  | Com Address | [5 empty] | Communicate addr ess |  |  |  |  | W | [5 empty] | 1
31 |  | FlashStart | [5 empty] | Update firmware |  |  |  |  | W | 0x0001:own 0X0100: TIC2000
32 |  | Reset User | [5 empty] | Reset User |  |  |  |  | W | 0x0001
|  | Info | [5 empty] | Information
33 |  | Reset to factory | [5 empty] | Reset to factory |  |  |  |  | W | 0x0001
34 |  | AutoTestSta rt | [5 empty] | AutoTestStart |  |  |  |  | W | 0x0001
35 |  | Vac low 2 | [5 empty] | Grid voltage low limit protect 2 |  |  |  |  | W |  |  |  | 0.1V
36 |  | Vac high 2 | [5 empty] | Grid voltage high limit protect 2 |  |  |  |  | W |  |  |  | 0.1V
37 |  | Fac low 2 | [5 empty] | Grid frequency low limit protect 2 |  |  |  |  | W |  |  |  | 0.01 Hz
38 |  | Fac high 2 | [5 empty] | Grid high frequency limit protect 2 |  |  |  |  | W |  |  |  | 0.01 Hz
39 |  | Vac low C | [5 empty] | Grid low voltage limit connect to Grid |  |  |  |  | W |  |  |  | 0.1V
40 |  | Vac high C | [5 empty] | Grid high voltage limit connect to Grid |  |  |  |  | W |  |  |  | 0.1V
41 |  | Fac low C | [5 empty] | Grid low frequency limit connect to Grid |  |  |  |  | W |  |  |  | 0.01 Hz
42 |  | Fac high C | [5 empty] | Grid high frequency limit connect to Grid |  |  |  |  | W |  |  |  | 0.01 Hz
43 |  | DTC | [5 empty] | Device Type Code | [5 empty] | &*6
44 |  | TP | [5 empty] | Input tracker num and output phase num | [5 empty] | Eg:0x0203 is two MPPT and 3ph output
45 |  | Sys Year | [5 empty] | System time-year |  |  |  |  | W | Year offset is 0
46 |  | Sys Month | [5 empty] | System time- Month |  |  |  |  | W
47 |  | Sys Day | [5 empty] | System time- Day |  |  |  |  | W
48 |  | Sys Hour | [5 empty] | System time- Hour |  |  |  |  | W
49 |  | Sys Min | [5 empty] | System time- Min |  |  |  |  | W
50 |  | Sys Sec | [5 empty] | System time- Second |  |  |  |  | W
51 |  | Vac low1 time | [5 empty] | Grid voltage low limit protect time 1 |  |  |  |  | W |  |  |  | Cycle
52 |  | Vac high1 time | [5 empty] | Grid voltage high limit protect time 1 |  |  |  |  | W |  |  |  | Cycle
53 |  | Vac low2 time | [5 empty] | Grid voltage low limit protect time 2 |  |  |  |  | W |  |  |  | Cycle
54 |  | Vac high2 time | [5 empty] | Grid voltage high limit protect time 2 |  |  |  |  | W |  |  |  | Cycle
55 |  | Fac low1 time | [5 empty] | Grid frequency low limit protect time 1 |  |  |  |  | W |  |  |  | Cycle
56 |  | Fac high1 time | [5 empty] | Grid frequency high limit protect time 1 |  |  |  |  | W |  |  |  | Cycle
57 |  | Fac low2 time | [5 empty] | Grid frequency low limit protect time 2 |  |  |  |  | W |  |  |  | Cycle
58 |  | Fac high2 time | [5 empty] | Grid frequency high limit protect time 2 |  |  |  |  | W |  |  |  | Cycle
59 |  | Manufactur er Info 8 | [5 empty] | Manufacturer information (high) | [8 empty] | ASCII
60 |  | Manufactur er Info 7 | [5 empty] | Manufacturer information (middle)
61 |  | Manufactur er Info 6 | [5 empty] | Manufacturer information (low)
62 |  | Manufactur er Info 5 | [5 empty] | Manufacturer information (high)
63 |  | Manufactur er Info 4 | [5 empty] | Manufacturer information (middle)
64 |  | Manufactur er Info3 | [5 empty] | Manufacturer information (low)
65 |  | Manufactur er Info 2 | [5 empty] | Manufacturer information (low)
66 |  | Manufactur er Info 1 | [5 empty] | Manufacturer information (high) | [8 empty] | ASCII
67 |  | FW Build No. 4 | [5 empty] | Control FW Build No. 2 | [8 empty] | ASCII
68 |  | FW Build No. 3 | [5 empty] | Control FW Build No. 1
69 |  | FW Build No. 2 | [5 empty] | COM FW Build No. 2
70 |  | FW Build No. 1 | [5 empty] | COM FW Build No. 1 | [8 empty] | ASCII
71
72 |  | Sys Weekly | [5 empty] | Sys Weekly |  |  |  |  | W | 0-6
73 |  | ModbusVer sion | [5 empty] | Modbus Version | [5 empty] | Eg ： 207 is V2.07 |  |  | Int(16 bits)
74 |  | ModelSelec ted | [5 empty] | Model Selected or not |  |  |  |  | W | 0: need to select; 1: have selected
75 |  | 232T485Ena ble | [5 empty] | 232T485Enable |  |  |  |  | W | 0: Disable; 1: Enable
76 |  | Decrease Power H | [5 empty] | Decrease output watt |  |  |  |  | W
77 |  | Decrease Power L | [5 empty] | Decrease output watt |  |  |  |  | W |  |  |  | 0.1W
78 |  | Increase Power H | [5 empty] | Increase output watt |  |  |  |  | W
79 |  | Increase Power L | [5 empty] | Increase output watt |  |  |  |  | W |  |  |  | 0.1W
80 |  | Factory | [5 empty] | The ODM Info code
81 |  | FreqDerateS tart | [5 empty] | Frequency derating start point |  |  |  |  | W |  |  |  | 0.01H Z
82 |  | LoadSpeed | [5 empty] | Load add speed |  |  |  |  | W |  |  |  | 0.1%
83 |  | 60HzLow | [5 empty] | 60Hz Fac low |  |  |  |  | W |  |  |  | 0.01H Z
84 |  | 60HzHingh | [5 empty] | 60Hz Fac hingh |  |  |  |  | W |  |  |  | 0.01H Z
85 |  | Vac start by pf | [5 empty] | Vac start adjust by pf |  |  |  |  | W |  |  |  | 0.1V
86 |  | PF of vac limit | [5 empty] | Max pf of adjust Vac |  |  |  |  | W | [5 empty] | 10000
87 |  | PID Working Model | [5 empty] | PID Working Model |  |  |  |  | W | 0:Automatic 1: Continual 2: Overnight
88 |  | PID On/Off Ctrl | [5 empty] | PID On/Off Control |  |  |  |  | W | 0:On 1:Off
89 |  | PID Volt Option | [5 empty] | PID Output Voltage Option |  |  |  |  | W | 300~1000 |  |  | V
90 |  | PFLineP1_L P | [5 empty] | PF limit line point 1 load percent |  |  |  |  | W | 0-255 |  |  | perce nt |  |  |  | 255 means no this point
91 |  | PFLineP1_P F | [5 empty] | PF limit line point 1 power factor |  |  |  |  | W | 0-20000
92 |  | PFLineP2_L P | [5 empty] | PF limit line point 2 load percent |  |  |  |  | W | 0-255 |  |  | perce nt |  |  |  | 255 means
no this point
93 |  | PFLineP2_P F | [5 empty] | PF limit line point 2power factor |  |  |  |  | W | 0-20000
94 |  | PFLineP3_L P | [5 empty] | PF limit line point 3 load percent |  |  |  |  | W | 0-255 |  |  | perce nt |  |  |  | 255 means no this point
95 |  | PFLineP3_P F | [5 empty] | PF limit line point 3 power factor |  |  |  |  | W | 0-20000
96 |  | PFLineP4_L P | [5 empty] | PF limit line point 4 load percent |  |  |  |  | W | 0-255 |  |  | perce nt |  |  |  | 255 means no this point
97 |  | PFLineP4_P F | [5 empty] | PF limit line point 4 power factor |  |  |  |  | W | 0-20000
98 |  | LCMDTest | [5 empty] | Local command test |  |  |  |  | W | 1 to test
99 |  | PFModel | [5 empty] | Set PF function Model |  |  |  |  | W | 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4： UnderExcite d (Inda) Reactive Power 5： OverExcited( Capa) Reactive Power 6： Q(v)model
100 |  | FLrate | [5 empty] | Frequency – load limit rate |  |  |  |  | W | 0-100 |  |  | 10tim es
101 |  | PFAdj1 | [5 empty] | PF adjust value 1 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
102 |  | PFAdj2 | [5 empty] | PF adjust value 2 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
103 |  | PFAdj3 | [5 empty] | PF adjust value 3 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
104 |  | PFAdj4 | [5 empty] | PF adjust value 4 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
105 |  | PFAdj5 | [5 empty] | PF adjust value 5 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
106 |  | PFAdj6 | [5 empty] | PF adjust value 6 | [5 empty] | 4096 is 1 | [6 empty] | Reserved
107 |  | LVFRTenabl e | [5 empty] | Low Voltage Fault Ride Through enable |  |  |  |  | W | 0 or 1
108 |  | V1S | [5 empty] | CEI021 V1S Q(v) |  |  |  |  | W | V1S<V2S |  |  | 0.1V
109 |  | V2S | [5 empty] | CEI021 V2S Q(v) |  |  |  |  | W |  |  |  | 0.1V
110 |  | V1L | [5 empty] | CEI021 V1L Q(v) |  |  |  |  | W | V1L<V1S |  |  | 0.1V
111 |  | V2L | [5 empty] | CEI021 V2L Q(v) |  |  |  |  | W | V2L<V1L |  |  | 0.1V
112 |  | U10min | [5 empty] | Volt protection for 10 min |  |  |  |  | W |  |  |  | 0.1V |  | 1.1Vn
113 |  | Qlockinpow er | [5 empty] | Q(v) lock in active power of CEI021 |  |  |  |  | W | 0-100 |  |  | Perce nt
114 |  | LIGridV | [5 empty] | Lock in gird volt of CEI021 PF line |  |  |  |  | W | nVn |  |  | 0.1V
115 |  | LOGridV | [5 empty] | Lock out gird volt of CEI021 PF line |  |  |  |  | W | nVn |  |  | 0.1V
116 |  | 6KwSystem | [5 empty] | Above 6KwSystem for CEI021 |  |  |  |  | W | 0 or 1
117 |  | FrequencyD eratingEnab le | [5 empty] | Frequency Derating Enable |  |  |  |  | W | 0 or 1 |  |  |  |  | 1
118 |  | QlockOutpo wer | [5 empty] | Q(v) lock Out active power of CEI021 |  |  |  |  | W | 0-100 |  |  | Perce nt
119 |  | RestartDela yTime | [5 empty] | Restart Delay Time after fault back; |  |  |  |  | W |  |  |  | s
120 |  | ReactiveRat e | [5 empty] | Reactive Rate in LVFRT |  |  |  |  | W | 0-100 |  |  |  |  | 2
121 |  | LVFRT_LV1 | [5 empty] | LVFRT low fault value 1 |  |  |  |  | W |  |  |  | 0.1V
122 |  | LVFRT_LT1 | [5 empty] | LVFRT low fault time 1 |  |  |  |  | W |  |  |  | 1ms
123 |  | LVFRT_LV2 | [5 empty] | LVFRT low fault value 2 |  |  |  |  | W |  |  |  | 0.1V
124 |  | LVFRT_LT2 | [5 empty] | LVFRT low fault time 2 |  |  |  |  | W |  |  |  | 1ms
125 |  | LVFRT_LV3 | [5 empty] | LVFRT low fault value 3 |  |  |  |  | W |  |  |  | 0.1V
126 |  | LVFRT_LT3 | [5 empty] | LVFRT low fault time 3 |  |  |  |  | W |  |  |  | 1ms
127 |  | LVFRT_LV4 | [5 empty] | LVFRT low fault value 4 |  |  |  |  | W |  |  |  | 0.1V
128 |  | LVFRT_LT4 | [5 empty] | LVFRT low fault time 4 |  |  |  |  | W |  |  |  | 1ms
129 |  | LVFRT_HV1 | [5 empty] | LVFRT high fault value 1 |  |  |  |  | W |  |  |  | 0.1V
130 |  | LVFRT_HT1 | [5 empty] | LVFRT high fault time 1 |  |  |  |  | W |  |  |  | 1ms
131 |  | wPowerRest artSlopeEE | [5 empty] | Power restart slope |  |  |  |  | W | 1-1000 |  |  | 0.1%
132 |  | wLoadDerat eStartVolt | [5 empty] | Load derate start ac voltage | [5 empty] | 1.05Vn~1.2V n |  |  | 0.1V
135 |  | SpecPasswo rdType | [5 empty] | Unlock or set Specpassword |  |  |  |  | W | 0:unlock ,au to lock in 5 minute; 1:change pw (should unlock first)， 2：lock, &*7 |  |  |  |  | 2
136 |  | SpecPasswo rd3 | [5 empty] | SpecPassword3 |  |  |  |  | W | For the spec setting change |  |  | ASCII |  | XX
137 |  | SpecPasswo rd2 | [5 empty] | SpecPassword2 |  |  |  |  | W | .. |  |  | ASCII |  | XX
138 |  | SpecPasswo rd1 | [5 empty] | SpecPassword1 |  |  |  |  | W | .. |  |  | ASCII |  | XX
139 |  | GTsetModel | [18 empty] | Reserved
140 |  | GFCI_old | [5 empty] | GFCI Module type | [5 empty] | 0 or 1, 1 is old | [6 empty] | Reserved
141 |  | DCIshift | [5 empty] | DCI offset | [5 empty] | Center is 30000 | [6 empty] | Reserved
142 |  | DCIAdj | [5 empty] | DCI adjust | [5 empty] | Center is 2000 | [6 empty] | Reserved
143 |  | Fast MPPT enable | [5 empty] | About Fast mppt | [5 empty] | 0,1,2 |  |  |  |  | 0 |  | Reserved
144 |  | IslandDisabl e | [5 empty] | IslandDisable |  |  |  |  | W | 0,1 |  |  |  |  | 0 |  | Reserved
145 |  | IniEEPROM | [5 empty] | IniEEPROM |  |  |  |  | W | 0xFF | [6 empty] | Reserved
146 |  | Balance 1 | [5 empty] | Phaseflag¦ErrorCod e |  |  |  |  | W | [7 empty] | Reserved
147 |  | Balance 2 | [5 empty] | Power H |  |  |  |  | W | [7 empty] | Reserved
148 |  | Balance 3 | [5 empty] | Power L |  |  |  |  | W | [7 empty] | Reserved
149 |  | bHighACVD erateSlope | [5 empty] | High ac voltage load derating slope |  |  |  |  | W | 20 |  |  | 0-100
150 |  | StartFanChe ck | [5 empty] | Start Fan Check |  |  |  |  | W | 1
151 |  | EnableNLin | [5 empty] | Enable N Line of grid |  |  |  |  | W | 1
e
152 |  | SimilarPVTr acker | [5 empty] | Similar PV strings for two trackers |  |  |  |  | W | 1
153 |  | wCheckHar dware | [5 empty] | wCheckHardware |  |  |  |  | W
154 |  | BlaneceMo del | [5 empty] | BlaneceModel |  |  |  |  | W | 1-3
155 |  | BalencePha se | [5 empty] | BalencePhase |  |  |  |  | W | 1-3
156 |  | DCIshift2 | [5 empty] | DCI offset 2 |  |  |  |  | W | Center is 30000 | [6 empty] | Reserved
157 |  | DCIshift3 | [5 empty] | DCI offset 3 |  |  |  |  | W | Center is 30000 | [6 empty] | Reserved
158 |  | EnergyLimit Enable | [5 empty] | Output Energy Limit Enable |  |  |  |  | R | 1 is enable | [6 empty] | Reserved
159 |  | EnergyRem ain H | [5 empty] | Output Energy Limit value High |  |  |  |  | W | 0.1kWh | [6 empty] | Reserved
160 |  | EnergyRem ain L | [5 empty] | Output Energy Limit value low |  |  |  |  | W | 0.1kWh | [6 empty] | Reserved
161 |  | BLVersion1 | [5 empty] | Boot loader version1 |  |  |  |  | R | [7 empty] | Reserved
162 |  | BLVersion2 | [5 empty] | Boot loader version2 |  |  |  |  | R | [7 empty] | Reserved
163 |  | TrakerMode l | [5 empty] | 2 Traker Model |  |  |  |  | W | 0,1,2 | [6 empty] | Reserved
164 |  | PMcheck | [5 empty] | Growatt Resaved |  |  |  |  | W | [7 empty] | Reserved
165 |  | QVRPDelayT imeEE | [5 empty] | QV Reactive Power delaytime |  |  |  |  | W | 0-30 |  |  | 1S |  | 3S
166 |  | OverFDerat DelayTimeE E | [5 empty] | Overfrequency der ating delaytime |  |  |  |  | W | 0-20 |  |  | 50ms |  | 0
167 |  | SoftstartFla g | [5 empty] | Softstart enable for Australia spec |  |  |  |  | W | 0: Disable 1: enable |  |  |  |  | 1
168 |  | QPercentM ax | [5 empty] | Qmax for Q(V) curve |  |  |  |  | W | 0-1000 |  |  | 0.1%
169 |  | DRMSEn | [5 empty] | DRMS enable for Australia spec |  |  |  |  | W | 0: Disable 1: enable |  |  |  |  | 0
170 |  | PowerVoltF uncEn | [5 empty] | Enable PowerVoltFuntion for SAA Spec |  |  |  |  | W | 0: Disable 1: enable |  |  |  |  | 1
171 |  | INVWorkMo de | [5 empty] | INV work mode set |  |  |  |  | W | 0:default 1:CV Mode |  |  |  |  | 0
2:CC Mode 3:CP Mode
172 |  | PV1VoltSet | [5 empty] | pv1 voltage set when CV Mode was chosed |  |  |  |  | W | StartPVVolt-HighPVVolt
173 |  | PV2VoltSet | [5 empty] | Pv2 voltage set when CV Mode was chosed |  |  |  |  | W | StartPVVolt-HighPVVolt
174 |  | BT1CurrRef Set | [5 empty] | BT1 current set when CC Mode was chosed |  |  |  |  | W | 0-MaxBTCur rent
175 |  | BT2CurrRef Set | [5 empty] | BT2current set when CC Mode was chosed |  |  |  |  | W | 0-MaxBTCur rent
176 |  | WattACVRe coverDelayT ime | [5 empty] | Delay time for power recovering when ac voltage getting normal |  |  |  |  | W | 3-90S
180 |  | DHCP Disable | [5 empty] | Disable LAN DHCP |  |  |  |  | W | 1:Disable DHCP; 0:Enable DHCP;
181 |  | HostIP H | [5 empty] | LAN Local IP part1&part2 |  |  |  |  | W | part1*256+ part2
182 |  | HostIP L | [5 empty] | LAN Local IP part3&part4 |  |  |  |  | W | part3*256+ part4
183 |  | PV Voltage High Fault | [5 empty] | PV Voltage High Fault |  |  |  |  | W | 900V~10000 V |  |  | 0.1V
184 |  | Vac low 3 | [5 empty] | Grid voltage low limit protect 3 |  |  |  |  | W |  |  |  | 0.1V
185 |  | Vac high 3 | [5 empty] | Grid voltage high limit protect 3 |  |  |  |  | W |  |  |  | 0.1V
186 |  | Vac low3 time | [5 empty] | Grid voltage low limit protect time 3 |  |  |  |  | W | 9 |  |  | Cycle
187 |  | Vac high3 time | [5 empty] | Grid voltage high limit protect time 3 |  |  |  |  | W | 9 |  |  | Cycle
188 |  | Fac low 3 | [5 empty] | Grid frequency low limit protect 3 |  |  |  |  | W | 5600-6000 |  |  | 0.01H z
189 |  | Fac high 3 | [5 empty] | Grid frequency high |  |  |  |  | W | 6000-6400 |  |  | 0.01H
[8 empty] | limit protect 3 | [8 empty] | z
190 |  | Fac low3 time | [5 empty] | Grid frequency low limit protect time 3 |  |  |  |  | W | 119-17999 |  |  | Cycle
191 |  | Fac high3 time | [5 empty] | Grid frequency high limit protect time 3 |  |  |  |  | W | 9-599 |  |  | Cycle
192 |  | ubNToGND DetectBit | [5 empty] | Dis/enable N to GND detect functhion |  |  |  |  | W | 1:enable 0:disable |  |  | Cycle |  | 1
193 |  | uwEnableSp ecSet | [5 empty] | Dis/enable appointed spec setting |  |  |  |  | W | 1:enable 0:disable |  |  | Binary |  | 0x000 0 |  | Bit 0: Hungary
194 |  | NonStdVacE nable | [5 empty] | Enable/Disable Nonstandard AC voltage range |  |  |  |  | w | 0-1; 0:Disable; 1:Enable; |  |  |  |  | 0 |  | 0:Disable Nonstan dard AC voltag e range; 1:Enable Nonstand ard AC voltag e range;
195 |  | ServerIP H | [5 empty] | ServerIP part1&part2 |  |  |  |  | W | part1*256+ part2 |  |  |  |  | 192* 256+ 168 |  | 192.168
196 |  | ServerIP L | [5 empty] | ServerIP part3&part4 |  |  |  |  | W | part3*256+ part4 |  |  |  |  | 3*25 6+35 |  | 3.35
197 |  | TxDataInter val | [5 empty] | TxDataInterval |  |  |  |  | W | 1~600 |  |  | 0.1 mins |  | 50 |  | 5mins
198 |  | ChkCode NO.1 | [5 empty] | Datalogger Check Code 1 |  |  |  |  | R |  |  |  | ASCII
199 |  | ChkCode NO.2 | [5 empty] | Datalogger Check Code 2 |  |  |  |  | R |  |  |  | ASCII
200 |  | ChkCode NO.3 | [5 empty] | Datalogger Check Code 3 |  |  |  |  | R |  |  |  | ASCII
859 |  | bISLDShiftD eltaEE | [5 empty] | Growatt Resaved |  |  |  |  | W | [7 empty] | Reserved
860 |  | bLowPointe r | [5 empty] | Growatt Resaved |  |  |  |  | W | [7 empty] | Reserved
4.2 Input Reg (Some of input Registers can be wrote by Manufacturer, write address offset is 0x1000, start at 0x1000. can not be wrote by customer.)
Reg iste r NO. | Variable Name | [7 empty] | Description | [6 empty] | Value |  | Unit |  | Note
0 | Inverter Status | [7 empty] | Inverter run state | [6 empty] | 0:waiting, 1:normal, 3:fault
1 | Ppv H | [7 empty] | Input power (high) | [8 empty] | 0.1W
2 | Ppv L | [7 empty] | Input power (low) | [8 empty] | 0.1W
3 | Vpv1 | [7 empty] | PV1 voltage | [8 empty] | 0.1V
4 | PV1Curr | [7 empty] | PV1 input current | [8 empty] | 0.1A
5 | PV1Watt H | [7 empty] | PV1 input watt (high) | [8 empty] | 0.1W
6 | PV1Watt L | [7 empty] | PV1 input watt (low) | [8 empty] | 0.1W
7 | Vpv2 | [7 empty] | PV2 voltage | [8 empty] | 0.1V
8 | PV2Curr | [7 empty] | PV2 input current | [8 empty] | 0.1A
9 | PV2Watt H | [7 empty] | PV2 input watt (high) | [8 empty] | 0.1W
10 | PV2Watt L | [7 empty] | PV2 input watt (low) | [8 empty] | 0.1W
11 | Pac H | [7 empty] | Output power (high) | [8 empty] | 0.1W
12 | Pac L | [7 empty] | Output power (low) | [8 empty] | 0.1W
13 | Fac | [7 empty] | Grid frequency | [8 empty] | 0.01 Hz
14 | Vac1 | [7 empty] | Three/single phase voltage |  |  |  |  | grid |  |  |  | 0.1V
15 | Iac1 | [7 empty] | Three/single phase output current |  |  |  |  | grid |  |  |  | 0.1A
16 | Pac1 H | [7 empty] | Three/single phase output watt (high) |  |  |  |  | grid |  |  |  | 0.1V A
17 | Pac1 L | [7 empty] | Three/single phase output watt (low) |  |  |  |  | grid |  |  |  | 0.1V A
18 | Vac2 | [7 empty] | Three phase grid voltage | [8 empty] | 0.1V
19 | Iac2 | [7 empty] | Three phase grid output current | [8 empty] | 0.1A
20 | Pac2 H | [7 empty] | Three phase grid output power (high) | [8 empty] | 0.1V A
21 | Pac2 L | [7 empty] | Three phase grid output power (low) | [8 empty] | 0.1V A
22 | Vac3 | [7 empty] | Three phase grid voltage | [8 empty] | 0.1V
23 | Iac3 | [7 empty] | Three phase grid output current | [8 empty] | 0.1A
24 | Pac3 H | [7 empty] | Three phase grid output power (high) | [8 empty] | 0.1V A
25 | Pac3 L | [7 empty] | Three phase grid output power (low) | [8 empty] | 0.1V A
26 | Energy today H | [7 empty] | Today (high) | generate |  |  | energy |  |  |  |  | 0.1K WH
27 | Energy today L | [7 empty] | Today generate energy today (low) | [8 empty] | 0.1K WH
28 | Energy total H | [7 empty] | Total (high) | generate |  |  | energy |  |  |  |  | 0.1K WH
29 | Energy total L | [7 empty] | Total (low) | generate |  |  | energy |  |  |  |  | 0.1K WH
30 | Time total H | [7 empty] | Work time total (high) | [8 empty] | 0.5S
31 | Time total L | [7 empty] | Work time total (low) | [8 empty] | 0.5S
32 | Temperature | [7 empty] | Inverter temperature | [8 empty] | 0.1C
33 | ISO fault Value | [7 empty] | ISO Fault value | [8 empty] | 0.1V
34 | GFCI fault Value | [7 empty] | GFCI fault Value | [8 empty] | 1mA
35 | DCI fault Value | [7 empty] | DCI fault Value | [8 empty] | 0.01 A
36 | Vpv fault Value | [7 empty] | PV voltage fault value | [8 empty] | 0.1V
37 | Vac fault Value | [7 empty] | AC voltage fault value | [8 empty] | 0.1V
38 | Fac fault Value | [7 empty] | AC frequency fault value | [8 empty] | 0.01 Hz
39 | Temperature fault Value | [7 empty] | Temperature fault value | [8 empty] | 0.1C
40 | Fault code | [7 empty] | Inverter fault bit | [6 empty] | &*1
41 | IPM Temperature | [7 empty] | The inside IPM in inverter Temperature | [8 empty] | 0.1C
42 | P Bus Voltage | [7 empty] | P Bus inside Voltage | [8 empty] | 0.1V
43 | N Bus Voltage | [7 empty] | N Bus inside Voltage | [8 empty] | 0.1V
44 | Check Step | [7 empty] | Product check step | [10 empty] | Reserved
45 | IPF | [7 empty] | Inverter output PF now | [6 empty] | 0-20000
46 | ResetCHK | [7 empty] | Reset check data | [6 empty] | 1 to reset |  |  |  | Reserved
47 | DeratingMode | [7 empty] | DeratingMode | [6 empty] | 0:no deratring; 1:PV; 2:; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; |  |  |  | “*”is Reserved
7:Control; 8:*LoadSpee d; 9:*OverBackB yTime;
48 | Epv1_today H | [7 empty] | PV Energy today
49 | Epv1_today L | [7 empty] | PV Energy today | [8 empty] | 0.1k Wh
50 | Epv1_total H | [7 empty] | PV Energy total
51 | Epv1_total L | [7 empty] | PV Energy total | [8 empty] | 0.1k Wh
52 | Epv2_today H | [7 empty] | PV Energy today
53 | Epv2_today L | [7 empty] | PV Energy today | [8 empty] | 0.1k Wh
54 | Epv2_total H | [7 empty] | PV Energy total
55 | Epv2_total L | [7 empty] | PV Energy total | [8 empty] | 0.1k Wh
56 | Epv_total H | [7 empty] | PV Energy total
57 | Epv_total L | [7 empty] | PV Energy total | [8 empty] | 0.1k Wh
58 | Rac H | [7 empty] | AC Reactive power
59 | Rac L | [7 empty] | AC Reactive power | [8 empty] | 0.1Va r
60 | E_rac_today H | [7 empty] | AC Reactive energy
61 | E_rac_today L | [7 empty] | AC Reactive energy | [8 empty] | 0.1kV arh
62 | E_rac_total H | [7 empty] | AC Reactive energy
63 | E_rac_ total L | [7 empty] | AC Reactive energy | [8 empty] | 0.1kV arh
64 | WarningCode | [7 empty] | Warning Code | [6 empty] | &*8
65 | WarningValue1 | [7 empty] | Warning Value of slave CPU
66 | RealOPPercent | [7 empty] | RealOPPercent | [8 empty] | 1%
67 | OPFullwatt H | [7 empty] | Out put full load watt high
68 | OPFullwatt L | [7 empty] | Out put full load watt low | [8 empty] | 0.1W
69 | WarningValue2 | [7 empty] | Warning Value of main CPU | [6 empty] | PV1ShortCirc uit: 0x0001 PV2ShortCirc uit: 0x0002 BT1DriverFaul t: 0x0004 BT2DriverFaul t: 0x0008
70 | V _String1 | [7 empty] | PV String1 voltage | [8 empty] | 0.1V
71 | Curr _String1 | [7 empty] | PV String1 current | [6 empty] | -15A~15A |  | 0.1A
72 | V _String2 | [7 empty] | PV String2 voltage | [8 empty] | 0.1V
73 | Curr _String2 | [7 empty] | PV String2 current | [6 empty] | -15A~15A |  | 0.1A
74 | V _String3 | [7 empty] | PV String3 voltage | [8 empty] | 0.1V
75 | Curr _String3 | [7 empty] | PV String3 current | [6 empty] | -15A~15A |  | 0.1A
76 | V _String4 | [7 empty] | PV String4 voltage | [8 empty] | 0.1V
77 | Curr _String4 | [7 empty] | PV String4 current | [6 empty] | -15A~15A |  | 0.1A
78 | V _String5 | [7 empty] | PV String5 voltage | [8 empty] | 0.1V
79 | Curr _String5 | [7 empty] | PV String5 current | [6 empty] | -15A~15A |  | 0.1A
80 | V _String6 | [7 empty] | PV String6voltage | [8 empty] | 0.1V
81 | Curr _String6 | [7 empty] | PV String6 current | [6 empty] | -15A~15A |  | 0.1A
82 | V _String7 | [7 empty] | PV String7 voltage | [8 empty] | 0.1V
83 | Curr _String7 | [7 empty] | PV String7 current | [6 empty] | -15A~15A |  | 0.1A
84 | V _String8 | [7 empty] | PV String8 voltage | [8 empty] | 0.1V
85 | Curr _String8 | [7 empty] | PV String8 current | [6 empty] | -15A~15A |  | 0.1A
86 | StrFault | [7 empty] | 0~16 | [6 empty] | &*1
87 | StrWarning | [7 empty] | 0~16 | [6 empty] | &*1
88 | StrBreak | [7 empty] | Bit0~7: String1~8 disconnect Bit8~15: Reserved | [6 empty] | &*1
89 | PIDFaultCode | [7 empty] | 0~16 | [6 empty] | &*1
90 | Grid Fault record 1 - code | [7 empty] | Grid Fault record 1 - code
91 | Grid Fault record 1 - year¦ month | [7 empty] | Grid Fault record 1 - year¦ month | [6 empty] | Year offset is 2000
92 | Grid Fault record 1 - day¦ hour | [7 empty] | Grid Fault record 1 - day¦ hour
93 | Grid Fault record 1 - min¦ sec | [7 empty] | Grid Fault record 1 - min¦ sec
94 | Grid Fault record 1-value | [7 empty] | Grid Fault record 1-value | [6 empty] | &*2
95 | Grid Fault record 2 - code | [7 empty] | Grid Fault record 2 - code
96 | Grid Fault record 2 - year¦ month | [7 empty] | Grid Fault record 2 - year¦ month | [6 empty] | Year offset is 2000
97 | Grid Fault record 2 - day¦ hour | [7 empty] | Grid Fault record 2 - day¦ hour
98 | Grid Fault record 2 - min¦ sec | [7 empty] | Grid Fault record 2 - min¦ sec
99 | Grid Fault record 2-value | [7 empty] | Grid Fault record 2-value
100 | Grid Fault record 3 - code | [7 empty] | Grid Fault record 3 - code
101 | Grid Fault record 3 - year¦ month | [7 empty] | Grid Fault record 3 - year¦ month | [6 empty] | Year offset is 2000
102 | Grid Fault record 3 - day¦ hour | [7 empty] | Grid Fault record 3 - day¦ hour
103 | Grid Fault record 3 - min¦ sec | [7 empty] | Grid Fault record 3 - min¦ sec
104 | Grid Fault record 3-value | [7 empty] | Grid Fault record 3-value
105 | Grid Fault record 4 - code | [7 empty] | Grid Fault record 4 - code
106 | Grid Fault record 4 - year¦ month | [7 empty] | Grid Fault record 4 - year¦ month | [6 empty] | Year offset is 2000
107 | Grid Fault record 4 - day¦ hour | [7 empty] | Grid Fault record 4 - day¦ hour
108 | Grid Fault record 4 - min¦ sec | [7 empty] | Grid Fault record 4 - min¦ sec
109 | Grid Fault record 4-value | [7 empty] | Grid Fault record 4-value
110 | Grid Fault record 5 - code | [7 empty] | Grid Fault record 5 - code
111 | Grid Fault record 5 - year¦ month | [7 empty] | Grid Fault record 5 - year¦ month | [6 empty] | Year offset is 2000
112 | Grid Fault record 5 - day¦ hour | [7 empty] | Grid Fault record 5 - day¦ hour
113 | Grid Fault record 5 - min¦ sec | [7 empty] | Grid Fault record 5 - min¦ sec
114 | Grid Fault record 5-value | [7 empty] | Grid Fault record 5-value
115 | PID PVA+ Voltage | [7 empty] | PID PVAPE Volt | [6 empty] | 0V~1000V |  | 0.1V
116 | PID PVA+ Current | [7 empty] | PID PVAPE Curr | [6 empty] | -10mA~10mA |  | 0.1A
117 | PID Status | [7 empty] | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reverse | [6 empty] | 1~3
118 | PID PVB+ Voltage | [7 empty] | PID PVBPE Volt | [6 empty] | 0V~1000V |  | 0.1V
119 | PID PVB+ Current | [7 empty] | PID PVBPE Curr | [6 empty] | -10mA~10mA |  | 0.1A
120 | PV3 Voltage | [7 empty] | PV3 input voltage
121 | PV3 Current | [7 empty] | PV3 input current
122 | PV3Watt H | [7 empty] | PV3 input watt (high)
123 | PV3Watt L | [7 empty] | PV3 input watt (low)
124 | Epv3_today H | [7 empty] | PV3 Energy today
125 | Epv3_today L | [7 empty] | PV3 Energy today
126 | Epv3_total H | [7 empty] | PV3 Energy total
127 | Epv3_total L | [7 empty] | PV3 Energy total
128 | Faultcode H | [7 empty] | Inverter fault code high | [6 empty] | &*8
129 | Faultcode L | [7 empty] | Inverter fault code low
…
…
133
134
135 | bTestProcess<<8 ¦ bAutoTestStep | [7 empty] | Auto test process or auto test step | [6 empty] | &*3
136 | wAutoTestResult | [7 empty] | Auto test result | [6 empty] | &*4
137 | cTestStepStop | [7 empty] | Auto test stop step | [6 empty] | &*4
138 | 0 | [7 empty] | 0 | [8 empty] | 0
139 | Value Limit | [7 empty] | Safety voltage/frequency limit value | [8 empty] | 0.1V
140 | Time Limit | [7 empty] | Safety time limit value | [8 empty] | 1ms
141 | Real value | [7 empty] | Real voltage/frequency value | [8 empty] | 0.1V
142 | Test value | [7 empty] | Auto testing voltage/frequency value | [8 empty] | 0.1V
143 | Test treat value | [7 empty] | Auto test voltage/frequency treat value | [8 empty] | 0.1V
144 | Test treat time | [7 empty] | Auto test treat time | [8 empty] | 1ms
145
146
…
…
….
178
179
180 | Inverter Error record 1 - code | [7 empty] | Inverter Error record 1 - code
181 | Inverter Error record 1 - year¦ month | [7 empty] | Inverter Error record 1 - year¦ month | [6 empty] | Year offset is 2000
182 | Inverter Error record 1 - day¦ hour | [7 empty] | Inverter Error record 1 - day¦ hour
183 | Inverter Error record 1 - min¦ | [7 empty] | Inverter Error record 1 - min¦ sec
sec
184 | Inverter Error record 1-value | [7 empty] | Inverter Error record 1-value
185 | Inverter Error record 2 - code | [7 empty] | Inverter Error record 2 - code
186 | Inverter Error record 2 - year¦ month | [7 empty] | Inverter Error record 2 - year¦ month | [6 empty] | Year offset is 2000
187 | Inverter Error record 2 - day¦ hour | [7 empty] | Inverter Error record 2 - day¦ hour
188 | Inverter Error record 2 - min¦ sec | [7 empty] | Inverter Error record 2 - min¦ sec
189 | Inverter Error record 2-value | [7 empty] | Inverter Error record 2-value
190 | Inverter Error record 2 - code | [7 empty] | Inverter Error record 2 - code
191 -41 9 | Inverter Error record…… | [7 empty] | Inverter Error record……
420 | Inverter Error record49 - code | [7 empty] | Inverter Error record 49- code
421 | Inverter Error record49 - year¦ month | [7 empty] | Inverter Error record49 - year¦ month | [6 empty] | Year offset is 2000
422 | Inverter Error record49 - day¦ hour | [7 empty] | Inverter Error record49 - day¦ hour
423 | Inverter Error record49 - min¦ sec | [7 empty] | Inverter Error record49 - min¦ sec
424 | Inverter Error record49-value | [7 empty] | Inverter Error record49-value
425 | Inverter Error record50 - code | [7 empty] | Inverter Error record 50- code
426 | Inverter Error record50 - year¦ month | [7 empty] | Inverter Error record50 - year¦ month | [6 empty] | Year offset is 2000
427 | Inverter Error record50 - day¦ hour | [7 empty] | Inverter Error record50 - day¦ hour
428 | Inverter Error record50 - min¦ | [7 empty] | Inverter Error record50 - min¦ sec
sec
429 | Inverter Error record50-value | [7 empty] | Inverter Error record50-value
430
…
450 | E_hour0 H | [7 empty] | Energy hourly of this day
451 | E_hour0 L | [7 empty] | Energy hourly of this day
452 | E_hour1 H | [7 empty] | Energy hourly of this day
453 | E_hour1 L | [7 empty] | Energy hourly of this day
454 | E_hour | [7 empty] | …
… | E_hour | [7 empty] | …
496 | E_hour23 H | [7 empty] | Energy hourly of this day
497 | E_hour23 L | [7 empty] | Energy hourly of this day
498 | E_ day0 H | [7 empty] | Energy of latest day
499 | E_day0 L | [7 empty] | Energy of latest day
500 | E_ day1 H | [7 empty] | Energy of latest 1st day
501 | E_ day1 L | [7 empty] | Energy of latest 1st day
502 | E_ day | [7 empty] | …
… | E_ day | [7 empty] | …
510 | E_ day 6 H | [7 empty] | Energy of latest 6 th day
511 | E_ day 6L | [7 empty] | Energy of latest 6 th day
512 | E_ month0 H | [7 empty] | Energy of latest month
513 | E_ month0 L | [7 empty] | Energy of latest month
514 | E_ month1 H | [7 empty] | Energy of latest 1st month
515 | E_ month1 L | [7 empty] | Energy of latest 1st month
516 | E_ month | [7 empty] | …
… | E_ month | [7 empty] | …
534 | E_ month11 H | [7 empty] | Energy of latest 11 th month
535 | E_ month11L | [7 empty] | Energy of latest 11 th month
536 | E_ year0 H | [7 empty] | Energy of latest year
537 | E_ year 0 L | [7 empty] | Energy of latest year
538 | E_ year 1 H | [7 empty] | Energy of latest 1st year
539 | E_ year 1 L | [7 empty] | Energy of latest 1st year
540 | E_ year | [7 empty] | …
… | E_ year | [7 empty] | …
574 | E_ year 19 H | [7 empty] | Energy of latest 11 th year
575 | E_ year19 L | [7 empty] | Energy of latest 11 th year
……. .
630 | Debug Resaved | [7 empty] | Debug Resaved | [10 empty] | Resaved
631 | Debug Resaved | [7 empty] | Debug Resaved | [10 empty] | Resaved
…. | Debug Resaved | [7 empty] | Debug Resaved | [10 empty] | Resaved
674 | Debug Resaved | [7 empty] | Debug Resaved | [10 empty] | Resaved
675 | Fault info. 0 | [7 empty] | The fault code info. 0 | [10 empty] | Resaved
676 | Fault info. 1 | [7 empty] | The fault code info. 1 | [10 empty] | Resaved
….. | Fault info. x | [7 empty] | The fault code info. x | [10 empty] | Resaved
706 | Fault info. 31 | [7 empty] | The fault code info. 31 | [10 empty] | Resaved
……. .
720 | Alarm info. 0 | [7 empty] | The Alarm code info. 0 | [10 empty] | Resaved
721 | Alarm info. 1 | [7 empty] | The Alarm code info. 1 | [10 empty] | Resaved
….. | Alarm info. x | [7 empty] | The Alarm code info. x | [10 empty] | Resaved
751 | Alarm info. 31 | [7 empty] | The Alarm code info. 31 | [10 empty] | Resaved
&*1: Inverter fault code Bit:
Fault type value | [6 empty] | Means(The message showed on the inverter when the inverter has fault)
1~23 | [6 empty] | " Error: 99+x ",
24 | [6 empty] | "Auto Test Failed",
25 | [6 empty] | "No AC Connection",
26 | [6 empty] | "PV Isolation Low",
27 | [6 empty] | " Residual I High",
28 | [6 empty] | " Output High DCI",
29 | [6 empty] | " PV Voltage High",
30 | [6 empty] | " AC V Outrange ",
31 | [6 empty] | " AC F Outrange ",
32 | [6 empty] | " Module Hot "
&*2: The value is 0.1V when the fault is the voltage, is 0.01Hz when the fault is the frequency; &*3:
|  | High byte value |  |  |  |  | Means |  |  |  |  | low byte value |  |  |  | Means
|  | 0 |  |  |  |  | Auto test stop |  |  |  |  | 0 |  |  |  | No test
|  | 1 |  |  |  |  | Auto test starting |  |  |  |  | 1 |  |  |  | Testing grid volt high pro
|  | 2 |  |  |  |  | Auto testing |  |  |  |  | 2 |  |  |  | Testing grid volt low pro
[12 empty] | 3 |  |  |  | Testing grid frequency high pro
[12 empty] | 4 |  |  |  | Testing grid frequency low pro
&*4: The variable “wAutoTestResult” and “cTestStepStop”: wAutoTestResult is the step test time
counter, when it reach cTestStepStop, this step test will stop and fail. &*5: Inverter Model: A , could be show: “T0 Q0 PF U1 M5 S1” or “00F151” Tx=(A&0XF00000)>>20 Qx=(A&0X0F0000)>>16 Px=(A&0x00F000)>>12 Ux=(A&0x000F00)>>8 Mx=(A&0x0000F0)>>4 Sx=(A&0x00000F) &*6: DTC(Device type code)
|  |  |  | Code No. |  |  |  | Device type |  |  | Note
|  |  |  | 001xx |  |  |  | Inverter |  |  | 1 tracker and 1phase Grid connect PV inverter TL
|  |  |  | 002xx |  |  |  | Inverter |  |  | 2 tracker and 1phase Grid connect PV inverter TL
|  |  |  | 003xx |  |  |  | Inverter |  |  | 1 tracker and 1phase Grid connect PV inverter HF
|  |  |  | 004xx |  |  |  | Inverter |  |  | 2 tracker and 1phase Grid connect PV inverter HF
|  |  |  | 005xx |  |  |  | Inverter |  |  | 1 tracker and 1phase Grid connect PV inverter LF
|  |  |  | 006xx |  |  |  | Inverter |  |  | 2 tracker and 1phase Grid connect PV inverter LF
|  |  |  | 007xx |  |  |  | Inverter |  |  | 1 tracker and 3phase Grid connect PV inverter TL
|  |  |  | 008xx |  |  |  | Inverter |  |  | 2 tracker and 3phase Grid connect PV inverter TL
|  |  |  | 009xx |  |  |  | Inverter |  |  | 1 tracker and 3phase Grid connect PV inverter LF
|  |  |  | 010xx |  |  |  | Inverter |  |  | 2 tracker and 3phase Grid connect PV inverter LF
……
|  |  |  | 10001 |  |  |  | Data logger |  |  | RF-ShineVersion
|  |  |  | 10002 |  |  |  | Data logger |  |  | Web-ShinePano
|  |  |  | 10003 |  |  |  | Data logger |  |  | Web-ShineWebBox
|  |  |  | 10004 |  |  |  | Data logger |  |  | WL-WIFI Module
……
|  |  |  | 11001 |  |  |  | Confluence box |  |  | Confluence box 1
……
&*7: Grid network power control command password: Inverter is in lock state after power on; change the power control by network command should unlock inverter first; default pw is XXXXXX; Unlock: send 0 to 3-135, then send password to 3-136~138; inverter will auto lock in 5min after unlocked; Change PW: unlock first, then send 1 to 3-135, then send new password to 3-136~138; Lock: send 0 or 2 to 3-135;
&*8: Inverter fault code and warning code
Fault code | [14 empty] | Warning code
0x00000001 |  |  |  |  | \ | [9 empty] | 0x0001 |  | Fan warning
0x00000002 |  |  |  |  | Communication error | [9 empty] | 0x0002 |  | String communication abnormal
0x00000004 |  |  |  |  | \ | [9 empty] | 0x0004 |  | StrPID config Warning
0x00000008 |  |  |  |  | StrReverse or StrShort fault | [9 empty] | 0x0008 |  | Fail to read EEPROM
0x00000010 |  |  |  |  | Model Init fault | [9 empty] | 0x0010 |  | DSP and COM firmware unmatch
0x00000020 |  |  |  |  | Grid Volt Sample diffirent | [9 empty] | 0x0020 |  | Fail to write EEPROM
0x00000040 |  |  |  |  | ISO Sample diffirent | [9 empty] | 0x0040 |  | SPD abnormal
0x00000080 |  |  |  |  | GFCI Sample diffirent | [9 empty] | 0x0080 |  | GND and N connect abnormal
0x00000100 |  |  |  |  | \ | [9 empty] | 0x0100 |  | PV1 or PV2 circuit short
0x00000200 |  |  |  |  | \ | [9 empty] | 0x0200 |  | PV1 or PV2 boost driver broken
0x00000400 |  |  |  |  | \ | [9 empty] | 0x0400 |  | \
0x00000800 |  |  |  |  | \ | [9 empty] | 0x0800 |  | \
0x00001000 |  |  |  |  | AFCI Fault | [9 empty] | 0x1000 |  | \
0x00002000 |  |  |  |  | \ | [9 empty] | 0x2000 |  | \
0x00004000 |  |  |  |  | AFCI Module fault | [9 empty] | 0x4000 |  | \
0x00008000 |  |  |  |  | \ | [9 empty] | 0x8000 |  | \
0x00010000 |  |  |  |  | \
0x00020000 |  |  |  |  | Relay check fault
0x00040000 |  |  |  |  | \
0x00080000 |  |  |  |  | \
0x00100000 |  |  |  |  | \
0x00200000 |  |  |  |  | Communication error
0x00400000 |  |  |  |  | Bus Voltage error
0x00800000 |  |  |  |  | AutoTest fail
0x01000000 |  |  |  |  | No Utility
0x02000000 |  |  |  |  | PV Isolation Low
0x04000000 |  |  |  |  | Residual I High
0x08000000 |  |  |  |  | Output High DCI
0x10000000 |  |  |  |  | PV Voltage high
0x20000000 |  |  |  |  | AC V Outrange
0x40000000 |  |  |  |  | AC F Outrange
0x80000000 |  |  |  |  | TempratureHigh
5 Set address
Refer to the Inverter user manual. Always is : Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you
can give a single knock to change the address, this address will be remembered when the lcd backlight off. 6 Notice 1) It can drive mostly 32 pv inverters for one rs485 comport. 2) There are only read input and hold registers commands even the newest version. 3) App user could only care the input register. 4) App user could not care the holding registers. 5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;