## Table 1
GROWATT INVERTER MODBUS RTU PROTOCOL_Ⅱ | [34 empty] | Version V1.39 Date 2024.04.16
Copyright © Shenzhen Growatt New Energy Co., Ltd. 2024. All rights reserved. No part of this document may be reproduced, stored in a retrieval system, or transmitted, in any form or by any means, be it electronic, mechanical, photographic, magnetic or otherwise, withou t the prior written per-mission of Shenzhen Growatt New Energy Co., Ltd.
SHENZHEN GROWATT NEW ENERGY CO.,LTD.
Address: Telephone: website: | [6 empty] | 4-13/Building A, Sino-German(Europe) industrial Park, Hangcheng Ave, Bao'an District, Shenzhen, China 400-931-9122 www.growatt.com ¦ service@ginverter.com
Version Record
Index | [5 empty] | Version | [8 empty] | Change content | [23 empty] | Author |  |  |  |  | Date
1 | [5 empty] | V1.00 | [8 empty] | First Republic | [23 empty] | Weiwei.shi |  |  |  |  | 2020-04-28
2 | [5 empty] | V1.25 | [8 empty] | Add backup box data register:input3281-3316. | [23 empty] | Liang.liu |  |  |  |  | 2022-05-13
3 | [5 empty] | V1.26 | [8 empty] | Modify the range of backup box error code(input3284) and warning code(input3285) value. | [23 empty] | Liang.liu |  |  |  |  | 2022-07-14
4 | [5 empty] | V1.27 | [8 empty] | 1.Add PTO enable register (holding3072); 2.Add Battery charge from generator function enable register (holding3073); 3.Add force generator on enable register (holding3074). | [23 empty] | Liang.liu |  |  |  |  | 2022-11-03
5 | [5 empty] | V1.28 | [8 empty] | 1.Add backup box enable register holding3082(for XH model); 2.Add Australian region parameter register holding3083(for XH model); 3.Add the grid parameter of the three-phase backup box register input3317-3319(for XH model); 4.Add backup box data display flag register holding3250 and input3321(for GW server); 5.Add the software version and serial number of backup box register holding3251-3268(for GW server); 6.Add backup box the communication status register input3320(for GW server); 7.Add derating modes in register input3086; 8.Add inverter hardware version register holding3046(for US model); | [23 empty] | Liang.liu |  |  |  |  | 2022-12-02
6 | [5 empty] | V1.29 | [8 empty] | 1. Modify the definition of GridFirstStopSOC(holding3037). 2.Add On-Grid Stop Discharging SOC register holding3067. 3.Add BDC new serial number and reserve registers holding7960-8559 (Support up to 10 parallel BDC). 4.Add inverter SN number flag register input3277(For US model). 5.Add battery SN number flag register input3278(For US model). 6.Add backup box SN number flag register input3279(For US model). 7. Add generator rated power parameter register holding3077 (For US model). | [23 empty] | Zhengjie.Liu |  |  |  |  | 2023-02-09
7 | [5 empty] | V1.30 | [8 empty] | 1.Add On-Grid Stop Discharging SOC register holding3082. | [23 empty] | Zhengjie.Liu |  |  |  |  | 2023-03-02
8 | [5 empty] | V1.31 | [8 empty] | 1. Modify the definition and Variable Name of GeneratorOnCmd register (holding3074). | [23 empty] | Zhengjie.Liu |  |  |  |  | 2023-03-24
9 | [5 empty] | V1.32 | [8 empty] | 1. Add APX battery register holding 5400-7959 and input | [23 empty] | Zhengjie.Liu |  |  |  |  | 2023-05-30
5080-7639. 2.Add AFCI software version register holding3269-3271. 3.Add Buzzer enable register holding645 4.Add Clear EMS time setting register holding3124. 5.Add Inverter total power-on time register input3116-3117.
10 | [5 empty] | V1.33 | [8 empty] | 1. Add Acrel meter connect flag register input3322. 2. Add backup box installation flag register input3323. 3.Add battery module new serial number register holding8560-9519. 4.Add BDC information register holding3112, holding3115-3121, | [23 empty] | Zhengjie.Liu |  |  |  |  | 2023-06-14
11 | [5 empty] | V1.34 | [8 empty] | 1.Add battery type register hold700. | [23 empty] | Kangju Lu |  |  |  |  | 2023-09-27
12 | [5 empty] | V1.35 | [8 empty] | Delete MIX model description and merge it into SPH model. | [23 empty] | Meilin.Luo |  |  |  |  | 2023-10-17
13 | [5 empty] | V1.36 | [8 empty] | 1.Add state 0x09 in Input register1000, 2.Add unit in Input register1149-1150. | [23 empty] | Ziqi.Kang |  |  |  |  | 2023-11-23
14 | [5 empty] | V1.37 | [8 empty] | 1.Add appendix table 1: Inverter derating mode (Input3086) and table 2: Battery derating mode (Input3165),update the inverter and battery derating mode. | [23 empty] | Liang.liu |  |  |  |  | 2024-01-29
15 | [5 empty] | V1.38 | [8 empty] | 1. Add hold355 as the DSP software debugging version number. 2. Add hold359 as the M3 software debugging version number. 3. Add hold3272-3274 busbar protection function parameters. 4. Add hold659 battery serial number setting lock. 5. Add input3324 off-grid box unbalanced current. 6. Add input3342 off-grid box inv relay status. 7. Add input3343 generator relay status. 8. Add hold3282 enter bypass mode enable register. 9. Add meter data registers (read through 0x20 function code). 10. Add holding192 bit1 as the inverter support 1024 bytes update flag. | [23 empty] | Zhengjie.Liu |  |  |  |  | 2024-04-08
16 | [5 empty] | V1.39 | [8 empty] | 1. Add scope WIT TL3. 2. Add hold875-999 as business storge power used by WIT TL3. 3. Add hold871 as Grid phase Sequence. 4. Add hold874 as Parallel enable. 5.Add input8000—9000 for business Storage Power | [23 empty] | Shuangshuang.Yang |  |  |  |  | 2024-04-16
Catalog 1 Introduction 6 1.1 Purpose 6 1.2 Scope 6 2 Protocol register 7 5.1 Hold register 7 5.2 Input register 62 3 Set address 119 4 Notice 120 5 Attachment 121 5.1 Data format 121 5.2 Command format 121 5.3 Device Message Transmission Mode / Framing 127 5.3.1 RTU Mode 127 5.3.2 Maximum Data Length Definition 127
1 Introduction 1.1 Purpose Register range for various types of inverter. 1.2 Scope TL-X/TL-XH/TL-XH US （ MIN Type ） :03 register range:0~124 、 3000~3124 、 3125~3249(TL-XHUS) 、 3250~3374;04 register range:3000~3124 、 3125~3249 、 3250~3374. TL3-X(MAX 、MID 、MAC Type):03 register range:0~124 、125~249;04 register range:0~124、125~249. MAX 1500V 、 MAX-X LV: 03 register range:0~124 、 125~249;04 register range:0~124、125~249、875~999. MOD TL3-XH: 03 register range:0~124,3000~3124 、 3250~3374; 04 register range:3000~3124、3125~3249、3250~3374. Storage(MIX Type):03 register range:0~124、1000~1124;04 register range:0~124、 1000~1124 Storage(SPA Type):03 register range:0~124 、 1000~1124;04 register range:1000~1124、2000~2124、1125~1249. Storage(SPH Type):03 register range:0~124、1000~1124;04 register range:0~124、 1000~1124、1125~1249. WIT TL3: 03 register range:0~124、125~249、875~999;04 register range:0~124、 125~249、8000~8124. 、
2 Protocol register It is 16 bits (two bytes) unsigned integer for each holding and input register. 2.1 Hold register
Regis ter NO. |  |  | Variable Name |  |  |  | Description | [11 empty] | Write /Rea d |  |  |  | Range | [5 empty] | Unit |  |  |  | Initial value |  |  |  | Note
First group
0 |  |  | OnOff |  |  |  | Remote On/Off . On（1）;Off（0） | [11 empty] | W |  |  |  | 0~3 | [9 empty] | 1 |  |  |  | The inverter can be switched on and off, and
[7 empty] | Inverter On（3）;Off（2） | [29 empty] | the BDC can be switched on and off for the batt
[7 empty] | BDC | [29 empty] | ready function.
1 |  |  | Safty |  |  |  | Bit0: SPI enable | [11 empty] | W | [17 empty] | 0 : disable,1: enable
|  |  | Function |  |  |  | Bit1: AutoTestStart | [29 empty] | SPI: system protection
|  |  | Enable |  |  |  | Bit2: LVFRT enable | [29 empty] | interface
[7 empty] | Bit3:FreqDerating | [29 empty] | Bit0~3:for CEI0-21
[7 empty] | Enable | [29 empty] | Bit4~6:for SAA
Bit4: Softstart
enable
Bit5: DRMS enable
Bit6:PowerVoltFun
c Enable
Bit7: HVFRT enable
Bit8:ROCOF enable
Bit9: Recover
FreqDeratingMode
Enable
Bit10:Split phase
Bit11: AC Couple
enable
Bit12~15:Reserve
2 |  |  | PF CMD |  |  |  | Set holding register | [11 empty] | W |  |  |  | 0~1 | [9 empty] | 0 |  |  |  | Meaning is these settings
|  |  | memory |  |  |  | 3,4,5,99 CMD will | [29 empty] | will be acting or not
|  |  | state |  |  |  | be set or not(1/0), | [29 empty] | when next power on
if not, these
settings are the
initial value.
3 |  |  | Active Power Rate |  |  |  | Inverter Max output active power percent | [11 empty] | W |  |  |  | 0-100 or255 | [5 empty] | % |  |  |  | 255 |  |  |  | 255: power limited |  |  |  |  | is | not | be
4 |  |  | Reactive Power Rate |  |  |  | Inverter max output reactive power percent | [11 empty] | W |  |  |  | -100-100 or 255 | [5 empty] | % |  |  |  | 255 |  |  |  | 255: power limited |  |  |  |  | is | not | be
5 |  |  | Power factor |  |  |  | Inverter output power factor’s 10000 times | [11 empty] | W |  |  |  | 0-20000 | [9 empty] | 0 |  |  |  | 0-10000 is underexcited, other is overexcited
6 |  |  | Pmax H |  |  |  | Normal (high) | [5 empty] | power | [15 empty] | 0.1VA
7 |  |  | Pmax L |  |  |  | Normal (low) | [5 empty] | power | [15 empty] | 0.1VA
8 |  |  | Vnormal |  |  |  | Normal work PV voltage | [21 empty] | 0.1V
9 |  |  | Fw version H |  |  |  | Firmware version (high) | [21 empty] | ASCII
10 |  |  | Fw version M |  |  |  | Firmware version (middle)
11 |  |  | Fw version L |  |  |  | Firmware version (low)
12 |  |  | Fw version2 H |  |  |  | Control Firmware version (high) | [21 empty] | ASCII
13 |  |  | Fw version2 M |  |  |  | Control Firmware version (middle)
14 |  |  | Fw version2 L |  |  |  | Control Firmware version (low)
15 |  |  | LCD language |  |  |  | LCD language | [11 empty] | W |  |  |  | 0-5 | [13 empty] | 0: Italian; 1: English; 2: German; 3: Spanish; 4: French; 5: Chinese; 6:Polish 7:Portugues 8:Hungary
16 |  |  | Country Selected |  |  |  | Country Selected or not | [11 empty] | W |  |  |  | 0~1 | [13 empty] | 0: need to select; 1: have selected
17 |  |  | Vpv start |  |  |  | Input start voltage | [11 empty] | W | [9 empty] | 0.1V
18 |  |  | Time start |  |  |  | Start time | [11 empty] | W | [9 empty] | 1s
19 |  |  | RestartDel ayTime |  |  |  | Restart Delay Time after fault back; | [11 empty] | W | [9 empty] | 1s
20 |  |  | Power Start Slope |  |  |  | Power start slope | [11 empty] | W |  |  |  | 1-1000 | [5 empty] | 0.1%
21 |  |  | Power Restart Slope |  |  |  | Power restart slope | [11 empty] | W |  |  |  | 1-1000 | [5 empty] | 0.1%
22 |  |  | Select Baud rate |  |  |  | Select communication baud rate | [11 empty] | W |  |  |  | 0-1 | [9 empty] | 0 |  |  |  | 0: 9600bps 1:38400bps
23 |  |  | Serial NO |  |  |  | Serial number 1-2 | [21 empty] | ASCII
24 |  |  | Serial NO |  |  |  | Serial number 3-4
25 |  |  | Serial NO |  |  |  | Serial number 5-6
26 |  |  | Serial NO |  |  |  | Serial number 7-8
27 |  |  | Serial NO |  |  |  | Serial number 9-10
28 |  |  | Module H |  |  |  | Inverter Module (high) | [15 empty] | &*5
29 |  |  | Module L |  |  |  | Inverter Module (low) | [15 empty] | &*5
30 |  |  | Com Address |  |  |  | Communicate ad dress | [11 empty] | W |  |  |  | 1-254 | [9 empty] | 1
31 |  |  | FlashStart |  |  |  | Update firmware | [11 empty] | W |  |  |  | 1
32 |  |  | Reset User Info |  |  |  | Reset User Information | [11 empty] | W |  |  |  | 0x0001
33 |  |  | Reset to factory |  |  |  | Reset to factory | [11 empty] | W |  |  |  | 0x0001
34 |  |  | Manufactu rer Info 8 |  |  |  | Manufacturer information (high) | [21 empty] | ASCII
35 |  |  | Manufactu rer Info 7 |  |  |  | Manufacturer information (middle)
36 |  |  | Manufactu rer Info 6 |  |  |  | Manufacturer information (low)
37 |  |  | Manufac.t urer Info 5 |  |  |  | Manufacturer information (high)
38 |  |  | Manufactu rer Info 4 |  |  |  | Manufacturer information (middle)
39 |  |  | Manufactu rer Info3 |  |  |  | Manufacturer information (low)
40 |  |  | Manufactu rer Info 2 |  |  |  | Manufacturer information (low)
41 |  |  | Manufactu rer Info 1 |  |  |  | Manufacturer information (high)
42 |  |  | bfailsafeEn ; |  |  |  | G100 fail safe | [11 empty] | W |  |  |  | 0~1 | [13 empty] | Enable:1,Disable:0 English G100 fail safe set
43 |  |  | DTC |  |  |  | Device Type Code | [15 empty] | &*6
44 |  |  | TP |  |  |  | Input tracker num and output phase num | [29 empty] | Eg:0x0203 is two MPPT and 3ph output
45 |  |  | Sys Year |  |  |  | System time-year | [11 empty] | W | [17 empty] | Local time, Year offset is 0
46 |  |  | Sys Month |  |  |  | System time- Month | [11 empty] | W
47 |  |  | Sys Day |  |  |  | System time- Day | [11 empty] | W
48 |  |  | Sys Hour |  |  |  | System time- Hour | [11 empty] | W
49 |  |  | Sys Min |  |  |  | System time- Min | [11 empty] | W
50 |  |  | Sys Sec |  |  |  | System time- Second | [11 empty] | W
51 |  |  | Sys Weekly |  |  |  | System Weekly | [11 empty] | W |  |  |  | 0~6
52 |  |  | Vac low |  |  |  | Grid voltage low limit protect | [11 empty] | W | [9 empty] | 0.1V
53 |  |  | Vac high |  |  |  | Grid voltage high limit protect | [11 empty] | W | [9 empty] | 0.1V
54 |  |  | Fac low |  |  |  | Grid frequency low limit protect | [11 empty] | W | [9 empty] | 0.01Hz
55 |  |  | Fac high |  |  |  | Grid high frequencylimit protect | [11 empty] | W | [9 empty] | 0.01Hz
56 |  |  | Vac low 2 |  |  |  | Grid voltage low limit protect 2 | [11 empty] | W | [9 empty] | 0.1V
57 |  |  | Vac high 2 |  |  |  | Grid voltage high limit protect 2 | [11 empty] | W | [9 empty] | 0.1V
58 |  |  | Fac low 2 |  |  |  | Grid frequency low limit protect 2 | [11 empty] | W | [9 empty] | 0.01Hz
59 |  |  | Fac high 2 |  |  |  | Grid high frequency limit protect 2 | [11 empty] | W | [9 empty] | 0.01Hz
60 |  |  | Vac low 3 |  |  |  | Grid voltage low limit protect 3 | [11 empty] | W | [9 empty] | 0.1V
61 |  |  | Vac high 3 |  |  |  | Grid voltage high limit protect 3 | [11 empty] | W | [9 empty] | 0.1V
62 |  |  | Fac low 3 |  |  |  | Grid frequency low limit protect 3 | [11 empty] | W | [9 empty] | 0.01Hz
63 |  |  | Fac high 3 |  |  |  | Grid frequency high limit protect 3 | [11 empty] | W | [9 empty] | 0.01Hz
64 |  |  | Vac low C |  |  |  | Grid low voltage limit connect to Grid | [11 empty] | W | [9 empty] | 0.1V
65 |  |  | Vac high C |  |  |  | Grid high voltage limit connect to Grid | [11 empty] | W | [9 empty] | 0.1V
66 |  |  | Fac low C |  |  |  | Grid low frequency limit connect to Grid | [11 empty] | W | [9 empty] | 0.01Hz
67 |  |  | Fac high C |  |  |  | Grid high frequency limit connect to Grid | [11 empty] | W | [9 empty] | 0.01Hz
68 |  |  | Vac low1 time |  |  |  | Grid voltage low limit protect time 1 | [11 empty] | W | [9 empty] | Cycle
69 |  |  | Vac high1 time |  |  |  | Grid voltage high limit protect time 1 | [11 empty] | W | [9 empty] | Cycle
70 |  |  | Vac low2 time |  |  |  | Grid voltage low limit protect time 2 | [11 empty] | W | [9 empty] | Cycle
71 |  |  | Vac high2 time |  |  |  | Grid voltage high limit protect time 2 | [11 empty] | W | [9 empty] | Cycle
72 |  |  | Fac low1 time |  |  |  | Grid frequency low limit protect time 1 | [11 empty] | W | [9 empty] | Cycle
73 |  |  | Fac high1 time |  |  |  | Grid frequency high limit protect time 1 | [11 empty] | W | [9 empty] | Cycle
74 |  |  | Fac low2 .time |  |  |  | Grid frequency low limit protect time 2 | [11 empty] | W | [9 empty] | Cycle
75 |  |  | Fac high2 time |  |  |  | Grid frequency high limit protect time 2 | [11 empty] | W | [9 empty] | Cycle
76 |  |  | Vac low3 time |  |  |  | Grid voltage low limit protect time 3 | [11 empty] | W | [9 empty] | Cycle
77 |  |  | Vac high3 time |  |  |  | Grid voltage high limit protect time 3 | [11 empty] | W | [9 empty] | Cycle
78 |  |  | Fac low3 time |  |  |  | Grid frequency low limit protect time 3 | [11 empty] | W | [9 empty] | Cycle
79 |  |  | Fac high3 time |  |  |  | Grid frequency high limit protect time 3 | [11 empty] | W | [9 empty] | Cycle
80 |  |  | U10min |  |  |  | Volt protection for 10 min | [11 empty] | W | [9 empty] | 0.1V |  |  |  | 1.1Vn
81 |  |  | PV Voltage High Fault |  |  |  | PV Voltage High Fault | [11 empty] | W | [9 empty] | 0.1V
82 |  |  | FW Build No. 5 |  |  |  | Model letter version number (TJ) | [21 empty] | ASCII
83 |  |  | FW Build No. 4 |  |  |  | Model letter version number (AA) | [21 empty] | ASCII
84 |  |  | FW Build No. 3 |  |  |  | DSP1 FW Build No. | [21 empty] | ASCII
85 |  |  | FW Build No. 2 |  |  |  | DSP2/M0 FW Build No. | [21 empty] | ASCII
86 |  |  | FW Build No. 1 |  |  |  | CPLD/AFCI FW Build No. | [21 empty] | ASCII
87 |  |  | FW Build No. 0 |  |  |  | M3 FW Build No. | [21 empty] | ASCII
88 |  |  | Modbus Version |  |  |  | Modbus Version | [21 empty] | Int(16b its) | [7 empty] | Eg:207 is V2.07
89 |  |  | PFModel |  |  |  | Set PF function Model | [11 empty] | W | [17 empty] | 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6:Q(v)model 7:Direct Control mode
8. Static capacitive QV mode
9. Static inductive QV mode
90 |  |  | GPRS IP Flag |  |  |  | Bit0-3:read: 1:Set GPRS IP Successed Write:2:Read GPRS IP Successed Bit4-7:GPRS status | [11 empty] | W | [17 empty] | Bit0-3:about GPRS IP SET Bit4-7:about GRPRS Status
91 |  |  | FreqDerat eStart |  |  |  | Frequency derating start point | [11 empty] | W | [9 empty] | 0.01Hz
92 |  |  | FLrate |  |  |  | Frequency – load limit rate | [11 empty] | W |  |  |  | 0-100 | [5 empty] | 10 times
93 |  |  | V1S |  |  |  | CEI021 V1S Q(v) | [11 empty] | W |  |  |  | V1S<V2S | [5 empty] | 0.1V
94 |  |  | V2S |  |  |  | CEI021 V2S Q(v) | [11 empty] | W | [9 empty] | 0.1V
95 |  |  | V1L |  |  |  | CEI021 V1L Q(v) | [11 empty] | W |  |  |  | V1L<V1S | [5 empty] | 0.1V
96 |  |  | V2L |  |  |  | CEI021 V2L Q(v) | [11 empty] | W |  |  |  | V2L<V1L | [5 empty] | 0.1V
97 |  |  | Qlockinpo wer |  |  |  | Q(v) lock in active power of CEI021 | [11 empty] | W |  |  |  | 0-100 | [5 empty] | %
98 |  |  | QlockOutp ower |  |  |  | Q(v) lock Out active power of CEI021 | [11 empty] | W |  |  |  | 0-100 | [5 empty] | %
99 |  |  | LIGridV |  |  |  | Lock in gird volt of CEI021 PF line | [11 empty] | W |  |  |  | nVn | [5 empty] | 0.1V
100 |  |  | LOGridV |  |  |  | Lock out gird volt of CEI021 PF line | [11 empty] | W |  |  |  | nVn | [5 empty] | 0.1V
101 |  |  | PFAdj1 |  |  |  | PF adjust value 1 | [15 empty] | 4096 is 1
102 |  |  | PFAdj2 |  |  |  | PF adjust value 2 | [15 empty] | 4096 is 1
103 |  |  | PFAdj3 |  |  |  | PF adjust value 3 | [15 empty] | 4096 is 1
104 |  |  | PFAdj4 |  |  |  | PF adjust value 4 | [15 empty] | 4096 is 1
105 |  |  | PFAdj5 |  |  |  | PF adjust value 5 | [15 empty] | 4096 is 1
106 |  |  | PFAdj6 |  |  |  | PF adjust value 6 | [15 empty] | 4096 is 1
107 |  |  | QVRPDela yTimeEE |  |  |  | QV Reactive Power delaytime | [11 empty] | W |  |  |  | 0-30 | [5 empty] | 1S |  |  |  | 3S
108 |  |  | OverFDera tDelayTim eEE |  |  |  | Overfrequency de ratingdelaytime | [11 empty] | W |  |  |  | 0-20 | [5 empty] | 50ms |  |  |  | 0
109 |  |  | Qpercent Max |  |  |  | Qmax for Q(V) curve | [11 empty] | W |  |  |  | 0-1000 | [5 empty] | 0.1%
110 |  |  | PFLineP1_ LP |  |  |  | PF limit line point 1 load percent | [11 empty] | W |  |  |  | 0-255 | [5 empty] | % | [7 empty] | 255 means no this point
111 |  |  | PFLineP1_ PF |  |  |  | PF limit line point 1 power factor | [11 empty] | W |  |  |  | 0-20000
112 |  |  | PFLineP2_ LP |  |  |  | PF limit line point 2 load percent | [11 empty] | W |  |  |  | 0-255 | [5 empty] | % | [7 empty] | 255 means no this point
113 |  |  | PFLineP2_ PF |  |  |  | PF limit line point 2power factor | [11 empty] | W |  |  |  | 0-20000
114 |  |  | PFLineP3_ LP |  |  |  | PF limit line point 3 load percent | [11 empty] | W |  |  |  | 0-255 | [5 empty] | % | [7 empty] | 255 means no this point
115 |  |  | PFLineP3_ PF |  |  |  | PF limit line point 3 power factor | [11 empty] | W |  |  |  | 0-20000
116 |  |  | PFLineP4_ LP |  |  |  | PF limit line point 4 load percent | [11 empty] | W |  |  |  | 0-255 | [5 empty] | % | [7 empty] | 255 means no this point
117 |  |  | PFLineP4_ PF |  |  |  | PF limit line point 4 power factor | [11 empty] | W |  |  |  | 0-20000
118 |  |  | Module 4 |  |  |  | Inverter Module (4) | [15 empty] | &*11 | [13 empty] | SxxBxx
119 |  |  | Module 3 |  |  |  | Inverter Module (3) | [15 empty] | &*11 | [13 empty] | DxxTxx
120 |  |  | Module 2 |  |  |  | Inverter Module (2) | [15 empty] | &*11 | [13 empty] | PxxUxx
121 |  |  | Module 1 |  |  |  | Inverter Module (1) | [15 empty] | &*11 | [13 empty] | Mxxxx Power
122 |  |  | ExportLimi t_En/dis |  |  |  | ExportLimit_En/dis | [11 empty] | R/W |  |  |  | 1/0 | [13 empty] | ExportLimit enable, 0: Disable exportLimit; 1: Enable 485 exportLimit; 2: Enable 232 exportLimit; 3: Enable CT exportLimit;
123 |  |  | ExportLimi tPowerRat e |  |  |  | ExportLimitPowerR ate | [11 empty] | R/W |  |  |  | -1000~+10 00 | [5 empty] | 0.1% | [7 empty] | ExportLimit PowerRate
124 |  |  | TrakerMod el |  |  |  | Traker Model | [11 empty] | W |  |  |  | 0~2 | [13 empty] | 0:Independent 1:DC Source 2:Parallel
Second group
125 |  |  | INV Type-1 |  |  |  | Inverter type-1 | [11 empty] | R | [9 empty] | ASCII | [7 empty] | Reserved
126 |  |  | INV Type-2 |  |  |  | Inverter type-2 | [11 empty] | R | [9 empty] | ASCII
127 |  |  | INV Type-3 |  |  |  | Inverter type-3 | [11 empty] | R | [9 empty] | ASCII
128 |  |  | INV Type-4 |  |  |  | Inverter type-4 | [11 empty] | R | [9 empty] | ASCII
129 |  |  | INV Type-5 |  |  |  | Inverter type-5 | [11 empty] | R | [9 empty] | ASCII
130 |  |  | INV Type-6 |  |  |  | Inverter type-6 | [11 empty] | R | [9 empty] | ASCII
131 |  |  | INV Type-7 |  |  |  | Inverter type-7 | [11 empty] | R | [9 empty] | ASCII
132 |  |  | INV Type-8 |  |  |  | Inverter type-8 | [11 empty] | R | [9 empty] | ASCII
133 |  |  | BLVersion1 |  |  |  | Boot loader version1 | [11 empty] | R | [17 empty] | Reserved
134 |  |  | BLVersion2 |  |  |  | Boot loader version2 | [11 empty] | R | [17 empty] | Reserved
135 |  |  | BLVersion3 |  |  |  | Boot loader version3 | [11 empty] | R | [17 empty] | Reserved
136 |  |  | BLVersion4 |  |  |  | Boot loader version4 | [11 empty] | R | [17 empty] | Reserved
137 |  |  | Reactive P ValueH |  |  |  | Reactive PowerH | [11 empty] | R/W | [9 empty] | 0.1var
138 |  |  | Reactive P ValueL |  |  |  | Reactive PowerL | [11 empty] | R/W | [9 empty] | 0.1var
139 |  |  | ReactiveO utputPriori tyEnable |  |  |  | Reactive Output Priority Enable | [11 empty] | R/W | [9 empty] | 0/1 | [7 empty] | 0:disable 1:enable
140 |  |  | Reactive P Value(Rati o) |  |  |  | Reactive Power Ratio | [11 empty] | R/W | [9 empty] | 0.1
……. | [36 empty] | Reserved
141 |  |  | SvgFunctio nEnable |  |  |  | Svg enable on night | [11 empty] | R/W | [9 empty] | 0/1 | [7 empty] | 0:disable 1:enable
142 |  |  | uwUnderF UploadPoi nt |  |  |  | UnderF Upload Point | [11 empty] | R/W | [9 empty] | 0.01Hz
143 |  |  | uwOFDera teRecover Point |  |  |  | OFDerate RecoverPoint | [11 empty] | R/W | [9 empty] | 0.01Hz
144 |  |  | uwOFDera teRecover DelayTime |  |  |  | OFDerate RecoverDelayTime | [11 empty] | R/W |  |  |  | 0-30000 | [5 empty] | 50ms
145 |  |  | ZeroCurre ntEnable |  |  |  | ZeroCurrent Enable | [11 empty] | R/W |  |  |  | 0-1
146 |  |  | uwZeroCur rentStaticl owVolt |  |  |  | ZeroCurrent StaticlowVolt | [11 empty] | R/W |  |  |  | 460-2300 | [5 empty] | 0.1V |  |  |  | 115V
147 |  |  | uwZeroCur rentStatic HighVolt |  |  |  | ZeroCurrent StaticHighVolt | [11 empty] | R/W |  |  |  | 2300-2760 | [5 empty] | 0.1V |  |  |  | 276V
148 |  |  | uwHVoltD erateHighP oint |  |  |  | HVoltDerate HighPoint | [11 empty] | R/W |  |  |  | 0-10000 | [5 empty] | 0.1V
149 |  |  | uwHVoltD erateLowP oint |  |  |  | HVoltDerate LowPoint | [11 empty] | R/W |  |  |  | 0-10000 | [5 empty] | 0.1V
150 |  |  | uwQVPow erStableTi me |  |  |  | QVPower Stable Time | [11 empty] | R/W |  |  |  | 0-600 | [5 empty] | 0.1S
151 |  |  | uwUnderF UploadSto pPoint |  |  |  | UnderF Upload StopPoint | [11 empty] | R/W | [9 empty] | 0.01HZ
152 |  |  | fUnderFre qPoint |  |  |  | Underfrequency load start point | [11 empty] | R/W |  |  |  | 4600-5000 | [5 empty] | 0.01Hz |  |  |  | 49.8 |  |  |  | CEI
153 |  |  | fUnderFre qEndPoint |  |  |  | Underfrequency down load end point | [11 empty] | R/W |  |  |  | 4600-5000 | [5 empty] | 0.01Hz |  |  |  | 49.1 |  |  |  | CEI
154 |  |  | fOverFreq Point |  |  |  | Over frequency loading start point | [11 empty] | R/W |  |  |  | 5000-5200 | [5 empty] | 0.01Hz |  |  |  | 50.2 |  |  |  | CEI
155 |  |  | fOverFreq EndPoint |  |  |  | Over frequency loading end point | [11 empty] | R/W |  |  |  | 5000-5200 | [5 empty] | 0.01Hz |  |  |  | 51.5 |  |  |  | CEI
156 |  |  | fUnderVolt Point |  |  |  | Undervoltage load shedding start point | [11 empty] | R/W |  |  |  | 1600-3000 | [5 empty] | 0.1V |  |  |  | 220 |  |  |  | CEI
157 |  |  | fUnderVolt EndPoint |  |  |  | Undervoltage derating end point | [11 empty] | R/W |  |  |  | 1600-3000 | [5 empty] | 0.1V |  |  |  | 207 |  |  |  | CEI
158 |  |  | fOverVoltP oint |  |  |  | Overvoltage loading start point | [11 empty] | R/W |  |  |  | 1600-3000 | [5 empty] | 0.1V |  |  |  | 230 |  |  |  | CEI
159 |  |  | fOverVoltE ndPoint |  |  |  | Overvoltage loading end point | [11 empty] | R/W |  |  |  | 1600-3000 | [5 empty] | 0.1V |  |  |  | 245 |  |  |  | CEI
160 |  |  | uwNomina lGridVolt |  |  |  | NominalGridVolt Select | [11 empty] | R/W |  |  |  | 0~3 | [13 empty] | UL
161 |  |  | uwGridWa ttDelay |  |  |  | GridWatt DelayTime | [11 empty] | R/W |  |  |  | 0~3000 | [5 empty] | 20ms | [7 empty] | UL
162 |  |  | uwReconn ectStartSlo pe |  |  |  | Reconnect StartSlope | [11 empty] | R/W |  |  |  | 1~1000 | [5 empty] | 0.1 | [7 empty] | UL
163 |  |  | uwLFRTEE |  |  |  | LFRT1 Freq | [11 empty] | R/W |  |  |  | 5500~650 0 | [5 empty] | 0.01Hz | [7 empty] | UL
164 |  |  | uwLFRTTi meEE |  |  |  | LFRT1 Time | [11 empty] | R/W | [9 empty] | 20ms | [7 empty] | UL
165 |  |  | uwLFRT2E E |  |  |  | LFRT2 Freq | [11 empty] | R/W |  |  |  | 5500~650 0 | [5 empty] | 0.01Hz | [7 empty] | UL
166 |  |  | uwLFRTTi me2EE |  |  |  | LFRT2 Time | [11 empty] | R/W | [9 empty] | 20ms | [7 empty] | UL
167 |  |  | uwHFRTEE |  |  |  | HFRT1 Freq | [11 empty] | R/W |  |  |  | 5500~650 0 | [5 empty] | 0.01Hz | [7 empty] | UL
168 |  |  | uwHFRTTi meEE |  |  |  | HFRT1 Time | [11 empty] | R/W | [9 empty] | 20ms | [7 empty] | UL
169 |  |  | uwHFRT2E E |  |  |  | HFRT2 Freq | [11 empty] | R/W |  |  |  | 5500~650 0 | [5 empty] | 0.01Hz | [7 empty] | UL
170 |  |  | uwHFRTTi me2EE |  |  |  | HFRT2 Time | [11 empty] | R/W | [9 empty] | 20ms | [7 empty] | UL
171 |  |  | uwHVRTEE |  |  |  | HVRT1 Volt | [11 empty] | R/W | [9 empty] | 0.001U n | [7 empty] | UL
172 |  |  | uwHVRTTi meEE |  |  |  | HVRT1 Time | [11 empty] | R/W | [9 empty] | 20ms | [7 empty] | UL
173 |  |  | uwHVRT2E E |  |  |  | HVRT2 Volt | [11 empty] | R/W | [9 empty] | 0.001U n | [7 empty] | UL
174 |  |  | uwHVRTTi me2EE |  |  |  | HVRT2 Time | [11 empty] | R/W | [9 empty] | 0.001U n | [7 empty] | UL
175 |  |  | uwUnderF UploadDel ayTime |  |  |  | UnderF UploadDelayTime | [11 empty] | R/W |  |  |  | 0-40 | [5 empty] | 50ms |  |  |  | 0s |  |  |  | 50549
176 |  |  | uwUnderF UploadRat eEE |  |  |  | UnderF UploadRate | [11 empty] | R/W | [17 empty] | 50549
177 |  |  | uwGridRes tart_H_Fre q |  |  |  | GridRestart HighFreq | [11 empty] | R/W |  |  |  | 5000~550 0 | [5 empty] | 0.01Hz | [7 empty] | 50549
178 |  |  | OverFDera tResponse Time |  |  |  | OverFDerat ResponseTime | [11 empty] | W/R |  |  |  | 0-500
179 |  |  | UnderFUpl oadRespo nseTime |  |  |  | UnderFUpload ResponseTime | [11 empty] | W/R |  |  |  | 0-500
Intelligent control reads relevant data, used to identify the logo 180-200
180 |  |  | MeterLink |  |  |  | Whether to elect the meter | [11 empty] | R/W | [17 empty] | 0: Missed, 1: Received
181 |  |  | OPT Number |  |  |  | Number of connection optimizers | [11 empty] | R/W |  |  |  | 0-64 | [13 empty] | The total number of optimizers connected to the inverter
182 |  |  | OPT ConfigOK Flag |  |  |  | Optimizer configuration completion flag | [11 empty] | R/W | [17 empty] | 0x00:Not configured success 0x01:Configuration is completed
183 |  |  | PvStrScan |  |  |  | String Num | [11 empty] | R/W |  |  |  | 0、8、16、 32 | [13 empty] | 0:Not support Other:PvString Num
184 |  |  | BDCLinkN um |  |  |  | BDC parallel Num | [11 empty] | R/W | [13 empty] | 0 |  |  |  | The number of BDCs connected to the current machine
185 |  |  | PackNum |  |  |  | Number of battery modules | [11 empty] | R | [17 empty] | Total number of battery modules currently associated with all BDCs
186 |  |  | Reserved
187 |  |  | VPPFuncti onEnableS tatus |  |  |  | VPP function enable status | [11 empty] | R | [17 empty] | 0:Disable 1:Enable
188 |  |  | DataLog Connect ServerStat us |  |  |  | dataLog Connect Server status | [29 empty] | 0:connection succeeded 1:Connection failed
…… | [36 empty] | Reserved
192 |  |  | INVAndCol lectorInter action Function |  |  |  | INV and collectorInteractio n function | [11 empty] | R | [17 empty] | Bit0: 0:collector not upload software version. 1:collector upload software version Bit1: 0:inv not support 1024 bytes update 1:inv support 1024 bytes update
…… | [36 empty] | Reserved
200 |  |  | Reserved | [33 empty] | Reserved
201 |  |  | PID Working Model |  |  |  | PID Operating mode | [11 empty] | W | [17 empty] | 0: automatic 1: continuous 2: All night
202 |  |  | PID On/Off Ctrl |  |  |  | PID Break control | [11 empty] | W | [17 empty] | 0:On 1:Off
203 |  |  | PID Volt Option |  |  |  | PID Output voltage option | [11 empty] | W |  |  |  | 300~1000 | [5 empty] | V
…… | [36 empty] | Reserved
209 |  |  | New Serial NO |  |  |  | Serial number 1-2 | [21 empty] | ASCII
210 |  |  | New Serial NO |  |  |  | Serial number 3-4 | [21 empty] | ASCII
211 |  |  | New Serial NO |  |  |  | Serial number 5-6 | [21 empty] | ASCII
212 |  |  | New Serial NO |  |  |  | Serial number 7-8 | [21 empty] | ASCII
213 |  |  | New Serial NO |  |  |  | Serial number 9-10 | [21 empty] | ASCII
214 |  |  | New Serial NO |  |  |  | Serial number 11-12 | [21 empty] | ASCII
215 |  |  | New Serial NO |  |  |  | Serial 13-14 | [5 empty] | number | [15 empty] | ASCII
216 |  |  | New Serial NO |  |  |  | Serial 15-16 | [5 empty] | number | [15 empty] | ASCII
217 |  |  | New Serial NO |  |  |  | Serial 17-18 | [5 empty] | number | [15 empty] | ASCII
218 |  |  | New Serial NO |  |  |  | Serial 19-20 | [5 empty] | number | [15 empty] | ASCII
219 |  |  | New Serial NO |  |  |  | Serial 21-22 | [5 empty] | number | [15 empty] | ASCII
220 |  |  | New Serial NO |  |  |  | Serial 23-24 | [5 empty] | number | [15 empty] | ASCII
221 |  |  | New Serial NO |  |  |  | Serial 25-26 | [5 empty] | number | [15 empty] | ASCII
222 |  |  | New Serial NO |  |  |  | Serial 27-28 | [5 empty] | number | [15 empty] | ASCII
223 |  |  | New Serial NO |  |  |  | Serial 29-30 | [5 empty] | number | [15 empty] | ASCII
…… | [36 empty] | Reserved
229 |  |  | EnergyAdj ust |  |  |  | Power generation incremental calibration coefficient | [11 empty] | W/R |  |  |  | 1-1000 | [5 empty] | 0.1% | [7 empty] | (Percent ratio)
230~249 for growatt debug setting
230 |  |  | IslandDisa ble |  |  |  | Island not. | [5 empty] | Disable or | [5 empty] | W |  |  |  | 0~1 | [9 empty] | 0 |  | 1:disable |  |  |  |  | 0:Enable
231 |  |  | FanCheck |  |  |  | Start Fan Check | [11 empty] | W |  |  |  | 1
232 |  |  | EnableNLi ne |  |  |  | Enable N Line of grid | [11 empty] | W |  |  |  | 1 | [9 empty] | 0
233 |  |  | CheckHard ware |  |  |  | Check Hardware | [27 empty] | Bit0: GFCI Break; Bit1:SPS Damage Bit8:Eeprom read warning Bit9:EE write warning ……
234 |  |  | CheckHard ware2 | [31 empty] | reserved
235 |  |  | NToGNDD etect |  |  |  | Dis/enable N to GND detect function | [11 empty] | W |  |  |  | 0-1 | [9 empty] | 1 |  | 1:enable 0:disable
236 |  |  | NonStdVac Enable |  |  |  | Enable/Disable Nonstandard Grid voltage range | [11 empty] | W |  |  |  | 0-2 | [9 empty] | 0 |  | 0:Disable; 1:Enable Voltgrade1 2:Enable Voltgrade2
237 |  |  | EnableSpe cSet |  |  |  | Disablse/enable appointed spec setting | [11 empty] | W | [9 empty] | Binary |  |  |  | 0x00 00 |  | Bit 0: Hungary 1:enable 0:disable
238 |  |  | Fast MPPT enable |  |  |  | About Fast mppt | [15 empty] | 0~2 | [9 empty] | 0 |  | Reserved
239 | [34 empty] | Reserved
240 |  |  | Check Step | [15 empty] | W
241 |  |  | INV-Lng |  |  |  | Inverter Longitude | [11 empty] | W | [15 empty] | Longitude
242 |  |  | INV-Lat |  |  |  | Inverter Latitude | [11 empty] | W | [15 empty] | Latitude
…… | [34 empty] | Reserved
304 |  |  | uwAntiBac kflowFailP owerLimit EE |  |  |  | Anti-backflow failure power percentage | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | Anti-backflow failure default setting power percentage
305 |  |  | Qloadspee d |  |  |  | Reactive loading speed | [11 empty] | R/W |  |  |  | 0-100 | [5 empty] | 1% | [5 empty] | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value
306 |  |  | ParallelAnt iBackflowE n |  |  |  | ParallelAnti-Backfl ow Enable | [11 empty] | R/W |  |  |  | 0-1 | [11 empty] | Parallel anti-Backflow open enable bit 1: enable 0:disable
307 |  |  | AntiBackfl owFailure ResponseT ime |  |  |  | AntiBackflowFailur e ResponseTime | [11 empty] | R/W |  |  |  | 1-5000 | [5 empty] | 1s | [5 empty] | AntiBackflow Failure Response Time
308 |  |  | ParallelAnt iBackflowP owerLimit EE |  |  |  | Parallel Anti-Back flow Power | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | Parallel AntiBackflow Power
limit value setting
309 |  |  | bISOCheck Cmd |  |  |  | ISO detection command | [11 empty] | R/W |  |  |  | 0-1 | [5 empty] | 1 | [5 empty] | ISO detection command
310 |  |  | bGPRSStat us |  |  |  | GPRS Status 1: module not working 2: no sim card 3: No internet 4. TCP not connecting to server 5. TCP connection succeeded | [11 empty] | R/W |  |  |  | 0-255 | [5 empty] | 1
311 |  |  | Qmax_Ind uctive |  |  |  | The inductive Qmax of the Q(V) curve | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
312 |  |  | Qmax_Cap active |  |  |  | The Capactive Qmax of the Q(V) curve | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
313 |  |  | ReactivePo werAdjust FailureRes ponseTim e |  |  |  | Reactive Power Adjust Failure Response Time | [11 empty] | R/W |  |  |  | 0-5000 | [5 empty] | S
314 |  |  | SuperAnti BackflowE nable |  |  |  | Super Anti-Back flow Enable | [11 empty] | R/W | [15 empty] | 0:disable,1:enable
315 |  |  | ReactivePo werStable Time |  |  |  | Reactive Power Stable Time | [11 empty] | R/W |  |  |  | 0-200 | [5 empty] | S
316 |  |  | QpStableTi me |  |  |  | QpStableTime | [11 empty] | R/W |  |  |  | 0-200 | [5 empty] | S
317 |  |  | PuDerateT ime |  |  |  | PuDerateTime | [11 empty] | R/W |  |  |  | 0-200 | [5 empty] | S
318 |  |  | QVModel Q2Point |  |  |  | QV mode Q2 set point reactive power percentage | [11 empty] | R/W |  |  |  | 0-2000 | [5 empty] | 0.1% | [5 empty] | Capacitive 30% （ The corresponding setting is 700);
319 |  |  | QVModel Q3Point |  |  |  | QV mode Q3 set point reactive power percentage | [11 empty] | R/W |  |  |  | 0-2000 | [5 empty] | 0.1% | [5 empty] | Inductive 30% (The corresponding setting is 1300); used for IEE1547
320 |  |  | VrefModel Enable |  |  |  | VrefModelEnable 0:Vref mode for QV curve is not active 1:Vref mode for QV curve is active | [11 empty] | R/W |  |  |  | 0/1 | [11 empty] | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted; When Vref mode is activated, V1~V4 of the QV curve are determined with Vref and cannot be changed, and Q1~Q4 can be modified by the host computer. Used for IEE1547
321 |  |  | uwVrefMo delFilterTi me |  |  |  | VrefModelFilterTi me | [11 empty] | R/W |  |  |  | 0-5000 | [5 empty] | S | [5 empty] | Activate Vref mode, the output filter value is equal to Vref with in the set time .Used for IEE1547
322 |  |  | uwUserQP ModeP1Kr ate |  |  |  | Active power P1 set point percentage for QP mode | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | used for IEE1547
323 |  |  | uwUserQP ModeP2Kr ate |  |  |  | Active power P2 set point percentage for QP mode | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | used for IEE1547
324 |  |  | uwUserQP ModeP3Kr ate |  |  |  | Active power P3 set point percentage for QP mode | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1% | [5 empty] | used for IEE1547
325 |  |  | uwUserQP ModeQ1Kr ate |  |  |  | Reactive power Q1 set point percentage for QP mode | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
326 |  |  | uwUserQP ModeQ2Kr ate |  |  |  | Reactive power Q2 set point percentage for QP mode | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
327 |  |  | uwUserQP ModeQ3Kr ate |  |  |  | Reactive power Q3 set point percentage for QP mode | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
328 |  |  | uwAcVolt HighDerat PowerLimi t |  |  |  | AcVoltHighDeratPo werLimit | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
329 |  |  | BackflowSi ngleCtrl |  |  |  | BackflowSingleCtrl | [11 empty] | R/W |  |  |  | 0: disable 1: enable
330 |  |  | bAntiBackf lowProtect Mode |  |  |  | AntiBackflowProte ctMode | [11 empty] | R/W |  |  |  | 0-3 | [11 empty] | Used for Australian
331 |  |  | uwUnderF UploadZer oPowerPoi nt |  |  |  | UnderfreqUploadZ eroPowerPoint | [11 empty] | W | [9 empty] | 0.01Hz
332 |  |  | FreqDerat eZeroPow erPoint |  |  |  | FreqDerateZeroPo werPoint | [11 empty] | W | [9 empty] | 0.01Hz
333 |  |  | bFreqDera tingStopM odeEnable |  |  |  | FreqDeratingStop ModeEnable | [11 empty] | R/W |  |  |  | 0-1
334 |  |  | bFreqIncre asingEnabl e |  |  |  | FreqIncreasingEna ble | [11 empty] | R/W |  |  |  | 0-1
335 |  |  | FreqIncrea singRecov erTime |  |  |  | FreqIncreasingRec overTime | [11 empty] | R/W | [9 empty] | 50ms
336 |  |  | FreqIncrea singEndLo wPoint |  |  |  | FreqIncreasingEnd LowPoint | [11 empty] | R/W | [9 empty] | 0.01Hz
337 |  |  | bFreqIncre asingStop ModeEnab le |  |  |  | FreqIncreasingStop ModeEnable | [11 empty] | R/W |  |  |  | 0-1
338 |  |  | UserQpCh rP1Krate |  |  |  | User QP function, charge P1 set point percentage | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
339 |  |  | UserQpCh rP2Krate |  |  |  | User QP function, charge P2 set point percentage | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
340 |  |  | UserQpCh rP3Krate |  |  |  | User QP function, charge P3 set point percentage | [11 empty] | R/W |  |  |  | 0-1000 | [5 empty] | 0.1%
341 |  |  | UserQpCh rQ1Krate |  |  |  | User QP function, charge Q1 set point percentage | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
342 |  |  | UserQpCh rQ2Krate |  |  |  | User QP function, charge Q2 set point percentage | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
343 |  |  | UserQpCh rQ3Krate |  |  |  | User QP function, charge Q3 set point percentage | [11 empty] | R/W |  |  |  | -1000-100 0 | [5 empty] | 0.1% | [5 empty] | -1000~1000:Inductive （100%）~ Capacitive（100%）
344 |  |  | FreqDerati ngRecover LowPoint |  |  |  | FreqDeratingRecov erLowPoint | [11 empty] | R/W | [9 empty] | 0.01HZ
345 |  |  | FreqIncrea singRecov erHighPoi nt |  |  |  | FreqIncreasingRec overHighPoint | [11 empty] | R/W | [9 empty] | 0.01HZ
…… | [34 empty] | Reserve
355 |  |  | DSPDebug FwVer |  |  |  | DSP debug software version | [11 empty] | R |  |  |  | 0-255
…… | [34 empty] | Reserve
359 |  |  | M3Debug FwVer |  |  |  | M3 debug software version | [11 empty] | R |  |  |  | 0-255
…… | [34 empty] | Reserve
532 |  |  | TurnOffUn loadSpeed |  |  |  | Turn Off Unload Speed | [11 empty] | W/R |  |  |  | 0-1000 | [9 empty] | 0.1% |  | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min
533 |  |  | LimitDevic e |  |  |  | Anti-backflow equipment selection | [11 empty] | W/R |  |  |  | 0-3 | [11 empty] | 1:Meter 3:CT Other:meaningless (Use for TL_XH)
534 |  |  | PowerSet OnDCSour ceMode |  |  |  | Power settings in dc source mode | [11 empty] | W/R |  |  |  | 0-90000 | [11 empty] | The unit is W (Use for TL_XH)
535 |  |  | OUFreqGr ade1En |  |  |  | Over-under-freque ncy Grade1Enable, currently only used by CEI0-21 | [11 empty] | W/R |  |  |  | 0-1 | [11 empty] | 0:disable 1:enable
536 |  |  | Country Set |  |  |  | Country settings under the same safety regulations | [11 empty] | W/R |  |  |  | 0-200 | [11 empty] | For mobile APP use only
538 |  |  | InterlockE nable |  |  |  | Three-machine communication Interlock function mode | [11 empty] | W/R |  |  |  | 0-2 | [11 empty] | 0:disable
1: Slave Enable 2. host enable
539 |  |  | OvTemper DeratePoi nt |  |  |  | Over temperature derate point | [11 empty] | W/R
540 |  |  | SafetySetP assword |  |  |  | Switch between different safety regulations to set the password | [11 empty] | W/R
541 |  |  | AFCI Onoff |  |  |  | AFCI Onoff | [11 empty] | W/R |  |  |  | 0xA0/0xA5 | [11 empty] | 0xA0:AFCI off 0xA5:AFCI on
542 |  |  | AfciSelfCh eck |  |  |  | Afci Self Check | [11 empty] | W/R | [15 empty] | 0:No self check 1: self check
543 |  |  | AfciReset |  |  |  | Afci Reset | [11 empty] | W/R | [15 empty] | 0:Not Reset 1: Reset
544 |  |  | AFCIValue 1 |  |  |  | AFCIThresholdValu e（low） | [11 empty] | W/R |  |  |  | 0-65000
545 |  |  | AFCIValue 2 |  |  |  | AFCIThresholdValu e（middle） | [11 empty] | W/R |  |  |  | 0-65000
546 |  |  | AFCIValue 3 |  |  |  | AFCIThresholdValu e（High） | [11 empty] | W/R |  |  |  | 0-65000
547 |  |  | OverThres holdValue MaxCnt |  |  |  | OverThresholdValu eMaxCnt | [11 empty] | W/R |  |  |  | 0-255
548 |  |  | AFCIScanT ypeEnable |  |  |  | AFCI curve scan type | [11 empty] | W/R |  |  |  | 1~4 | [11 empty] | 1:A road strength 2:A road FFT value 3:B road strength 4:B road FFT value
549 |  |  | PowerVolt StopMode En |  |  |  | PowerVoltStopMo deEn | [11 empty] | W/R |  |  |  | 0、1 | [11 empty] | 0:disable 1:enable
The power is restored when the voltage is less than the recovery point
550 |  |  | VoltWattR ecoverTim e |  |  |  | Voltage active power recovery time | [11 empty] | W/R |  |  |  | 0-15000 | [5 empty] | 20ms
551 |  |  | HVoltDerat eStopPow er |  |  |  | Voltage active cut-off power | [11 empty] | W/R |  |  |  | -5000-114 00
552 |  |  | QVTimeEx ponent |  |  |  | QV Time Exponent | [11 empty] | WR |  |  |  | 1-255 | [11 empty] | Q varies exponentially with time
553 |  |  | Volt-Watt Watt1 |  |  |  | Voltage active V1 point, corresponding active power | [11 empty] | WR |  |  |  | 0-11400
554 |  |  | Volt-Watt Watt2 |  |  |  | Voltage active V2 point, corresponding active power | [11 empty] | WR |  |  |  | 0-11400
…… | [34 empty] | Reserve
600 |  |  | Volt-Var Var1 |  |  |  | Voltage reactive V1 point, Corresponding reactive power percentage(Capaci tive | [11 empty] | WR |  |  |  | 0-1000 | [11 empty] | 0%~100.0%,US latest safety regulations
Qmax)
601 |  |  | Volt-Var Var2 |  |  |  | Voltage reactive V2 point,Correspondin g reactive power percentage | [11 empty] | WR |  |  |  | 0-1000 | [11 empty] | 0%~100.0%,US latest safety regulations
602 |  |  | Volt-Var Var3 |  |  |  | Voltage reactive V3 point,Correspondin g reactive power percentage | [11 empty] | WR |  |  |  | 0-1000 | [11 empty] | 0%~100.0%,US latest safety regulations
603 |  |  | Volt-Var Var4 |  |  |  | Voltage reactive V4 point,Correspondin g reactive power per-centage(Induct ive Qmax) | [11 empty] | WR |  |  |  | 0-1000 | [11 empty] | 0%~100.0%,US latest safety regulations
604 |  |  | Reserve | [31 empty] | Reserve
605 |  |  | OPModEn ergize |  |  |  | Allowed inverter output power | [11 empty] | R/W |  |  |  | 0/1 | [11 empty] | 0: output power not allowed 1: allowable output power For US models
608 |  |  | OneKeySet BDCMode |  |  |  | One key to set battery mode function | [11 empty] | R/W | [15 empty] | 0: self-use 1: battery priority 2: Grid priority 255:Disable Currently used for US models
609 |  |  | PowerOut putEnable |  |  |  | Zero Power Output Enable | [27 empty] | 0:Zero Power Output 1:Unlimited output power (default is 1)
610 |  |  | DealDebug ParaFlag |  |  |  | Flag bit for clearing debug variables | [27 empty] | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear
…… | [34 empty] | Reserve
645 |  |  | BuzzerOn Off |  |  |  | Buzzer enable/disable | [11 empty] | R/W |  |  |  | 0/1 | [11 empty] | 0:Disable buzzer 1:Enable buzzer(default)
…… | [34 empty] | Reserve
659 |  |  | BatSNSetti ngLock |  |  |  | Bat serial number setting lock | [11 empty] | R/W |  |  |  | 0/1 | [9 empty] | 0 |  | 0:locked 1:unlocked （ return 0 after setting bat serial number）
660 |  |  | ReloadCm d |  |  |  | M3 remote command | [27 empty] | 0xA0: Initialize safety defaults 0xAA: Reboot M3 remotely
…… | [34 empty] | Reserve
700 |  |  | bBMSType |  |  |  | Indicates the type of battery connected to the inverter | [27 empty] | 0: ARO battery 1: LG version 3 battery 2: APX HV battery 3: LG version 4 battery
871 |  |  | GridPhase Sequence | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:Positive order 1:Reverse order
874 |  |  | ParallelEna ble | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:disable 1:enable
875---------999 for business Storage Power
875 |  |  | FW Build No. 5 |  |  |  | ATS Model letter version number （MB） | [21 empty] | ASCII | [5 empty] | ATS version number
876 |  |  | FW Build No. 4 |  |  |  | ATS Model letter versionnumber （AA） | [21 empty] | ASCII | [5 empty] | ATS version number
877 |  |  | FW Build No. 3 |  |  |  | ATS-DSP1 FW Build No | [21 empty] | ASCII
878 |  |  | FW Build No. 2 |  |  |  | ATS-DSP2/M3 FW Build No | [21 empty] | ASCII
879 |  |  | ProductSet Enable | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:disable 1:enable
897 |  |  | ReConnTi mGridRest ore |  |  |  | Wait time for the grid to be restored and reconnected | [11 empty] | R/W |  |  |  | 0-65536 | [5 empty] | 1s |  |  |  | 300s
900 |  |  | STSEnable | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:disable 1:enable
901 |  |  | OilEnable | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:disable 1:enable
902 |  |  | OnOffCha ngeMode |  |  |  | Toggle modes | [11 empty] | R/W |  |  |  | 0-2 | [11 empty] | 0:-H 1:-EP 2:-UP
903 |  |  | PcsType | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:Optical storage all-in-one machine 1:Energy storage machine
904 |  |  | uwBattTyp e | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:Directly attach 1:DC-DC
905 |  |  | uwACChar gePowerR ate |  |  |  | AC allow charge Power Rate | [11 empty] | R/W |  |  |  | 0-100
906 |  |  | uwBattMa xChargeVo l |  |  |  | Battery Max charge voltage | [11 empty] | R/W | [11 empty] | X10
907 |  |  | uwBattEO DVol |  |  |  | Battery End of Discharge voltage | [11 empty] | R/W | [11 empty] | X10
908 |  |  | uwConnec tPhaseMo de |  |  |  | On Grid wireMode | [11 empty] | R/W | [15 empty] | 0:3p3w |  |  |  |  | 1:3p4w
909 |  |  | uwDisCon nectPhase Mode |  |  |  | Off Grid wireMode | [11 empty] | R/W | [15 empty] | 0:3p3w |  |  |  |  | 1:3p4w
910 |  |  | uwBatMax ChargeCur rent |  |  |  | Battery chargeCurrent | [9 empty] | Max |  | R/W | [11 empty] | X10
911 |  |  | uwBatMax DisCharge Current |  |  |  | Battery Max Discharge Current | [11 empty] | R/W | [11 empty] | X10
912 |  |  | uwOnOffC hangeMan ualMode |  |  |  | OnOffGrid Change Mode | [11 empty] | R/W | [15 empty] | 0:auto 1:manual
913 |  |  | uwOnOffG ridSet |  |  |  | OnOffGrid Set | [11 empty] | R/W | [15 empty] | 0:on grid 1:off grid （use for manual mode）
914 |  |  | uwOffGrid SoftStartE nable |  |  |  | OffGrid volt Start Enable | [9 empty] | Soft |  | R/W | [15 empty] | 0:disable, 1:enable
915 |  |  | uwOffgrid SoftStartTi me |  |  |  | Off grid volt soft start time | [11 empty] | R/W |  |  |  | 2~20 | [7 empty] | X10 |  |  |  | Unit （s）
917 |  |  | uwBatCap |  |  |  | Bat cap | [11 empty] | R/W
918 |  |  | uwPowerD ispatchEna ble |  |  |  | Vpp enable | [11 empty] | R/W | [15 empty] | 0:disable, 1:enable
919 |  |  | uwPowerD ispatchActi vePowerSe t |  |  |  | Power Dispatch Active Power Set | [11 empty] | R/W | [11 empty] | X10
936 |  |  | uwOffGrid Vol |  |  |  | Off grid volt | [11 empty] | R/W | [11 empty] | X10 |  |  |  | 0:220v 1:230v 2:240v 3:277v 4:127v
937 |  |  | uwOffGrid Freq |  |  |  | Off grid frequency | [11 empty] | R/W | [11 empty] | X10 |  |  |  | 0:50HZ;1:60HZ
938 |  |  | uwLoadPvI nverter |  |  |  | PCS Load Port has Invert or not | [11 empty] | R/W | [15 empty] | 0:No 1:Yes
939 |  |  | uwDgStart Soc |  |  |  | The soc point Start oil engine on Off grid | [11 empty] | R/W
940 |  |  | uwDgStop Soc |  |  |  | The soc point close oil engine on Off grid | [11 empty] | R/W
941 |  |  | uwLoadPvI nvStartFre q |  |  |  | The invert On load port Over frequency derating point | [11 empty] | R/W | [11 empty] | 0.0 1Hz
942 |  |  | uwLoadPvI nvFreqDer ateRate |  |  |  | The invert On load port Over frequency derating slope | [11 empty] | R/W
943 |  |  | uwLoadPvI nvFreqDer ateMinPo wer |  |  |  | the invert On load port Over frequency derating Min power | [11 empty] | R/W | [11 empty] | 0.1 kw
944 |  |  | uwDeman dMangeDi sChargePo werLimit |  |  |  | Demand management AC port discharge limit power | [11 empty] | R/W | [11 empty] | 1k w
945 |  |  | uwDeman dMangeCh argePower Limit |  |  |  | Demand management AC port charge limit power | [11 empty] | R/W | [11 empty] | 1k w
946 |  |  | uwDeman dMangeEn able |  |  |  | Demand management enable | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
947 |  |  | uwPowerU nblanceCtr lEnable |  |  |  | AC Power unbalance ctrl enable | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
948 |  |  | PcsParallel Num |  |  |  | Pcs parallel num | [11 empty] | R/W
949 |  |  | uwACChar geEnable |  |  |  | AC charge enable | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
950 |  |  | uwOffGrid Enable |  |  |  | Off grid enable | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
951 |  |  | uwBatChar geStopSoc |  |  |  | Battery charge stop SOC | [11 empty] | R/W | [11 empty] | 0~1 00
952 |  |  | uwBatDisC hargeStop Soc |  |  |  | Battery discharge stop SOC | [11 empty] | R/W | [11 empty] | 0~1 00
953 |  |  | uwSingleP haseAntiB ackflowEn able |  |  |  | Single phase AntiBackflow | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
954 |  |  | Time 1 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0:load first; 1:battery first; 2:grid first; bit15, 0:disable; 1:enable;
955 |  |  | Time 1 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12:hours;
956 |  |  | Time 1 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
957 |  |  | Time 2 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0: load first; 1: battery first; 2: grid first; bit15, 0:disable; 1:enable;
958 |  |  | Time 2 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
959 |  |  | Time 2 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
960 |  |  | Time 3 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0: load first; 1: battery first; 2: grid first; bit15, 0:disable; 1:enable;
961 |  |  | Time 3 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
962 |  |  | Time 3 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minute; bit8~12: hour;
963 |  |  | Time 4 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0: load first; 1: battery first; 2: grid first; bit15, 0:disable; 1:enable;
964 |  |  | Time 4 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
965 |  |  | Time 4 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minute; bit8~12: hour;
966 |  |  | Time 5 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0: load first; 1: battery first; 2: grid first; bit15, 0:disable; 1:enable;
967 |  |  | Time 5 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
968 |  |  | Time 5 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
969 |  |  | Time 6 Enable | [15 empty] | R/W | [15 empty] | bit13~14, 0: load first; 1: battery first; 2: grid first; bit15, 0:disable; 1:enable;
970 |  |  | Time 6 start time |  |  |  | Start Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
971 |  |  | Time 6 end time |  |  |  | End Time | [11 empty] | R/W | [15 empty] | bit0~7: minutes; bit8~12: hours;
972 |  |  | BMS Enable | [15 empty] | R/W | [15 empty] | 0:disable 1:enable
973 |  |  | parallel Enable |  |  |  | uwParallelEnable | [11 empty] | R/W | [15 empty] | 0:disable 1:enable
974 |  |  | BatCharge PowerLimi t |  |  |  | Battle Charge Power Limit | [11 empty] | R/W | [11 empty] | X10 |  |  |  | Unit （kw）
975 |  |  | BatDisChar gePowerLi mit |  |  |  | Battle DisCharge Power Limit | [11 empty] | R/W | [11 empty] | X10 |  |  |  | Unit （kw）
976 |  |  | ATS SpecPowe r |  |  |  | ATS SpecPower | [11 empty] | R/W | [11 empty] | 0.0 1 |  |  |  | Unit w
987 |  |  | ESPConstN CEnable |  |  |  | Emergency stop and normal closure are enabled, which distinguishes between the American version and the European version | [11 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:Valid low 1:Valid high
988 |  |  | MachineTy pe | [15 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:WIT 1:WIS
989 |  |  | ForcePowe rSlowChan ge |  |  |  | Power is forcibly slowly enabled | [11 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:DISABLE 1:ENABLE
990 |  |  | ForceChrD ischrPowe r[TIME1] |  |  |  | Time period 1 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
991 |  |  | ForceChrD ischrPowe r[TIME2] |  |  |  | Time period 2 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
992 |  |  | ForceChrD ischrPowe r[TIME3] |  |  |  | Time period 3 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
993 |  |  | ForceChrD ischrPowe r[TIME4] |  |  |  | Time period 4 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
994 |  |  | ForceChrD ischrPowe r[TIME5] |  |  |  | Time period 5 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
995 |  |  | ForceChrD ischrPowe r[TIME6] |  |  |  | Time period 6 power setting, only WIS models are allowed to set | [11 empty] | R/W |  |  |  | 0-100
996 |  |  | BakSoc | [15 empty] | R/W |  |  |  | 0-100 | [9 empty] | 50
997 |  |  | BakSocEna ble |  |  |  | The standby SOC is enabled under the demand management function | [11 empty] | R/W |  |  |  | 0-1 | [11 empty] | 0:DISABLE 1:ENABLE
998 |  |  | OffGridDis ChgStopSo c | [15 empty] | R/W |  |  |  | 0-100 | [9 empty] | 10
Six group for Storage Power
Regis ter NO. |  |  | Variable Name |  |  |  | Description | [11 empty] | Write /read |  |  |  | Range | [5 empty] | Unit |  |  |  | Initial value |  |  |  | Note
1000 |  |  | Float charge current limit |  |  |  | When charge current battery need is lower than this value, enter into float charge | [11 empty] | W | [9 empty] | 0.1A |  |  |  | 600 |  |  |  | CC current
1001 |  |  | PF CMD memory state |  |  |  | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | [11 empty] | W |  |  |  | 0~1 | [9 empty] | 0 |  |  |  | Means these settings will be acting or not when next power on(02 repeat)
1002 |  |  | VbatStartF orDischarg e |  |  |  | LV Vbat | [11 empty] | R/W | [9 empty] | 0.1V | [7 empty] | Lead-acid battery LV voltage
1003 |  |  | VbatlowW arnClr |  |  |  | Load Percent(only lead-Acid): 45.5V:<20%, 48.0V:20%~50% 49.0V:>50 | [11 empty] | W | [9 empty] | 0.1V | [7 empty] | Clear battery low voltage error voltage point
1004 |  |  | Vbatstopfo rdischarge |  |  |  | Should stop dischar-ge when lower than this voltage (only lead-Acid): 46.0V:<20% 44.8V:20%~50% 44.2V:>50% | [11 empty] | W | [9 empty] | 0.01V
1005 |  |  | Vbat stop for charge |  |  |  | Should stop charge when higher than this voltage | [11 empty] | W | [9 empty] | 0.01V |  |  |  | 5800
1006 |  |  | Vbatstartf ordischarg e |  |  |  | Should not discharge when lower than this voltage | [11 empty] | W | [9 empty] | 0.01V |  |  |  | 4800
1007 |  |  | Vbat constant charge |  |  |  | Can charge when lower than this voltage | [11 empty] | W | [9 empty] | 0.01V |  |  |  | 5800 |  |  |  | CV voltage（acid）
1008 |  |  | EESysInfo. SysSetEn |  |  |  | Bit0:Resved; Bit1:Resved; Bit2:Resved; Bit3:Resved; Bit4:Resved; Bit5:bDischargeEn; Bit6:ForceDischrEn ; Bit7:ChargeEn; Bit8:bForceChrEn; Bit9:bBackUpEn; Bit10:bInvLimitLoa dE; Bit11:bSpLimitLoad En; Bit12:bACChargeEn ; Bit13:bPVLoadLimi tEn; Bit14,15:UnUsed; | [11 empty] | W | [17 empty] | System Enable
1009 |  |  | Battemp lower limit d |  |  |  | Battery temperature lower limit for discharge | [11 empty] | W |  |  |  | 0-200, 1000-1400 | [5 empty] | 0.1℃ |  |  |  | 1170 |  |  |  | 0-200:0-20℃, 1000-1400:-40-0℃
1010 |  |  | Battemp upper limit d |  |  |  | Battery temperature upper limit for discharge | [11 empty] | W |  |  |  | 200-1000 | [5 empty] | 0.1℃ |  |  |  | 420
1011 |  |  | Battemp lower limit c |  |  |  | Battery temperature lower limit for charge | [11 empty] | W |  |  |  | 0-200:0-20 ℃ 1000-1400 :-40-0℃ | [5 empty] | 0.1℃ |  |  |  | 30 |  |  |  | Lower temperature limit
1012 |  |  | Battemp upper limit c |  |  |  | Battery temperature upper limit for charge | [11 empty] | W |  |  |  | 200-1000 | [5 empty] | 0.1℃ |  |  |  | 370 |  |  |  | Upper temperature limit
1013 |  |  | uwUnderF reDischarg eDelyTime |  |  |  | Under Fre Delay Time | [15 empty] | 0-20s | [5 empty] | 50ms | [7 empty] | Under Fre Delay Time
1014 |  |  | BatMdlSer ialNum |  |  |  | Battery serial number | [11 empty] | W |  |  |  | 00:00 | [13 empty] | SPH4-11K used
1015 |  |  | BatMdlPar allNum |  |  |  | Battery parallel section | [11 empty] | W |  |  |  | 00:00 | [13 empty] | SPH4-11K used
1016 |  |  | DRMS_EN | [33 empty] | 0:disable 1:enable
1017 |  |  | Bat First Start Time 4 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1018 |  |  | Bat First Stop Time 4 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1019 |  |  | BatFirst on/off Switch 4 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Battery priority enable 1
1020 |  |  | Bat First Start Time 5 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1021 |  |  | Bat First Stop Time 5 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1022 |  |  | BatFirst on/off Switch 5 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Battery priority enable 1
1023 |  |  | Bat First Start Time 6 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1024 |  |  | Bat First Stop Time 6 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1025 |  |  | BatFirst on/off Switch 6 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Battery priority enable 1
1026 |  |  | Grid First Start Time 4 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1027 |  |  | Grid First Stop Time 4 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1028 |  |  | Grid First Stop Switch 4 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Grid priority enable
1029 |  |  | Grid First Start Time 5 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1030 |  |  | Grid First Stop Time 5 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1031 |  |  | Grid First Stop Switch 5 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Grid priority enable
1032 |  |  | Grid First Start Time 6 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1033 |  |  | Grid First Stop Time 6 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1034 |  |  | Grid First Stop Switch 6 |  |  |  | Enable:1 Disable:0 | [15 empty] | 0 or 1 | [13 empty] | Grid priority enable
1035 |  |  | Bat First Start Time 4 |  |  |  | High eight:hours Low eight: minutes | [15 empty] | 0-23 0-59
1036 | [36 empty] | Reserve
1037 |  |  | bCTMode |  |  |  | Use the CTMode to Choose RFCT \ Cable CT\METER | [11 empty] | W |  |  |  | 0-2 | [9 empty] | 0 |  |  |  | 2:METER 1:WirelessCT 0:WiredCT
1038 |  |  | CTAdjust |  |  |  | CTAdjust enable | [11 empty] | W |  |  |  | 0/1 | [9 empty] | 0 |  |  |  | 0:disable,1:enable
…… | [36 empty] | Reserve
1044 |  |  | Priority |  |  |  | ForceChrEn/ForceD ischrEn Load first/bat first /grid first | [11 empty] | R |  |  |  | 0-2 | [13 empty] | bForceChrEn/disbForceDis chrEn/dis 0.Load(default)/1.Battery/ 2.Grid
1045 |  |  | Reserve
1046 |  |  | Reserve | [33 empty] | Reserve
1047 |  |  | AgingTestS tep Cmd |  |  |  | Command for aging test | [15 empty] | 0-2 | [13 empty] | Cmd for aging test 0: default,1: charge,2: discharge
1048 |  |  | BatteryTyp e |  |  |  | Battery type choose of buck-boost input | [15 empty] | 0-2 | [9 empty] | 0 |  |  |  | Battery type 0:Lithium,1:Lead-acid,2:ot her
1049 |  |  | Reserve | [33 empty] | Reserve
1060 |  |  | BuckUpsF unEn |  |  |  | Ups function enable or disable | [20 empty] | 0/1 | [11 empty] | 0:disable,1:enable
1061 |  |  | BuckUPSV oltSet |  |  |  | UPS output voltage | [20 empty] | 0-2 | [8 empty] | 230V |  |  | 0:230,1:208,2:240
1062 |  |  | UPSFreqSe t |  |  |  | UPS output frequency | [20 empty] | 0/1 | [8 empty] | 50Hz |  |  | 0:50Hz,1:60Hz
…… | [39 empty] | Reserve
Priority set
1070 |  |  | GridFirstDi schargePo werRate |  |  |  | Discharge Power Rate when Grid First | [17 empty] | W |  |  | 0-100 |  |  |  |  | 1% | [6 empty] | Discharge Power Rate when Grid First
1071 |  |  | GridFirstSt opSOC |  |  |  | Stop Discharge SOC when Grid First | [17 empty] | W |  |  | 0-100 |  |  |  |  | 1% | [6 empty] | Stop Discharge soc when Grid First
…… | [39 empty] | Reserve
1080 |  |  | Grid First Start Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1081 |  |  | Grid First Stop Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1082 |  |  | Grid First Stop Switch 1 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | Grid First enable
1083 |  |  | Grid First Start Time 2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1084 |  |  | Grid First Stop Time 2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1085 |  |  | Grid First Stop Switch 2 |  |  |  | ForceDischarge.bSwitch&LC D_SET_FORCE_TRUE_2)==L CD_SET_FORCE_TRUE_2 | [20 empty] | 0 or 1 | [8 empty] | Grid First enable |  |  | ForceDischarge; LCD_SET_FORCE_T RUE_2
1086 |  |  | Grid First Start Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1087 |  |  | Grid First Stop Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1088 |  |  | Grid First Stop Switch 3 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | Grid First enable
1089 | [39 empty] | reserve
1090 |  |  | BatFirstPo werRate |  |  |  | Charge Power Rate when Bat First | [17 empty] | W |  |  | 0-100 |  |  |  |  | 1% | [6 empty] | Charge Power Rate when Bat First
1091 |  |  | wBatFirst stop SOC |  |  |  | Stop Charge soc when Bat First | [17 empty] | W |  |  | 0-100 |  |  |  |  | 1% | [6 empty] | Stop Charge soc when Bat First
1092 |  |  | AC charge Switch |  |  |  | When Bat First Enable:1 Disable:0 | [20 empty] | Enable:1 Disable: 0 | [11 empty] | AC Charge Enable
…… | [39 empty] | Reserve
1100 |  |  | Bat First Start Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1101 |  |  | Bat First Stop Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1102 |  |  | BatFirst on/off Switch 1 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | Bat First Enable1
1103 |  |  | Bat First Start Time 2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1104 |  |  | Bat First Stop Time 2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1105 |  |  | BatFirston /off Switch 2 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | Bat First Enable2
1106 |  |  | Bat First Start Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1107 |  |  | Bat First Stop Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59
1108 |  |  | BatFirston /off Switch 3 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | Bat First Enable3
1109 | [39 empty] | Reserve
1110 |  |  | Load First Start Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1111 |  |  | Load First Stop Time 1 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1112 |  |  | Load First Switch 1 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | SPA/ reserve Load First Enable
1113 |  |  | Load First Start Time2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1114 |  |  | Load First Stop Time 2 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1115 |  |  | Load First Switch 2 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | SPA/ reserve Load First Enable
1116 |  |  | Load First Start Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1117 |  |  | Load First Stop Time 3 |  |  |  | High eight bit:hour Low eight bit:minute | [20 empty] | 0-23 0-59 | [11 empty] | SPA/ reserve
1118 |  |  | Load First Switch 3 |  |  |  | Enable :1 Disable:0 | [20 empty] | 0 or 1 | [11 empty] | SPA/ reserve Load First Enable
1119 |  |  | NewEPow erCalcFlag | [36 empty] | 0:The old formula 1:The new formula
1120 |  |  | BackUpEn |  |  |  | BackUp Enable | [32 empty] | SPH6K US
1121 |  |  | SGIPEn |  |  |  | SGIP Enable | [32 empty] | SPH6K US
…… | [39 empty] | Reserve
1125 |  |  | BatSerialN O. 8 |  |  |  | Product serial number of the first PACK of energy storage batteries | [25 empty] | ASCII
1126 |  |  | BatSerialN O. 7 | [29 empty] | ASCII
1127 |  |  | BatSerialN O. 6 | [29 empty] | ASCII
1128 |  |  | BatSerialN O. 5 | [29 empty] | ASCII
1129 |  |  | BatSerialN O. 4 | [29 empty] | ASCII
1130 |  |  | BatSerialN O. 3 | [29 empty] | ASCII
1131 |  |  | BatSerialN O. 2 | [29 empty] | ASCII
1132 |  |  | BatSerialN O. 1 | [29 empty] | ASCII
1132 ~120 4 |  |  | Bat Serial NO.8~ Bat Serial NO. 1 |  |  |  | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and the format of the serial number of each PACK is 1125 to 1132 | [25 empty] | ASCII
…… |  |  | Reserve
1244 |  |  | Com version NameH |  |  |  | Name of the battery main control firmware version | [25 empty] | ASCII
1245 |  |  | Com version NameL |  |  |  | Name of the battery main control firmware version | [25 empty] | ASCII
1246 |  |  | Com version No |  |  |  | Version of the battery main control firmware | [25 empty] | digital
1247 |  |  | Com version NameH |  |  |  | Name of battery monitoring firmware version | [25 empty] | ASCII
1248 |  |  | Com version NameL |  |  |  | Name of battery monitoring firmware version | [25 empty] | ASCII
1249 |  |  | Com version No |  |  |  | Battery monitoring firmware version | [25 empty] | digital
Use for TL-X and TL-XH
3000 |  |  | ExportLimi tFailedPow erRate |  |  |  | The power rate when exportLimit failed | [17 empty] | R/W | [7 empty] | 0.1% | [6 empty] | The power rate when export Limit failed
3001 |  |  | New Serial NO |  |  |  | Serial number 1-2 | [17 empty] | R/W | [7 empty] | ASCII | [6 empty] | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters.
3002 |  |  | New Serial NO |  |  |  | Serial number 3-4 | [17 empty] | R/W | [7 empty] | ASCII
3003 |  |  | New Serial NO |  |  |  | Serial number 5-6 | [17 empty] | R/W | [7 empty] | ASCII
3004 |  |  | New Serial NO |  |  |  | Serial number 7-8 | [17 empty] | R/W | [7 empty] | ASCII
3005 |  |  | New Serial NO |  |  |  | Serial number 9-10 | [17 empty] | R/W | [7 empty] | ASCII
3006 |  |  | New Serial NO |  |  |  | Serial number 11-12 | [17 empty] | R/W | [7 empty] | ASCII
3007 |  |  | New Serial NO |  |  |  | Serial number 13-14 | [17 empty] | R/W | [7 empty] | ASCII
3008 |  |  | New Serial NO |  |  |  | Serial number 15-16 | [17 empty] | R/W | [7 empty] | ASCII
3009 |  |  | New Serial NO |  |  |  | Serial number 17-18 | [17 empty] | R/W | [7 empty] | ASCII
3010 |  |  | New Serial NO |  |  |  | Serial number 19-20 | [17 empty] | R/W | [7 empty] | ASCII
3011 |  |  | New Serial NO |  |  |  | Serial number 21-22 | [17 empty] | R/W | [7 empty] | ASCII
3012 |  |  | New Serial NO |  |  |  | Serial number 23-24 | [17 empty] | R/W | [7 empty] | ASCII
3013 |  |  | New Serial NO |  |  |  | Serial number 25-26 | [17 empty] | R/W | [7 empty] | ASCII
3014 |  |  | New Serial NO |  |  |  | Serial number 27-28 | [17 empty] | R/W | [7 empty] | ASCII
3015 |  |  | New Serial NO |  |  |  | Serial number 29-30 | [17 empty] | R/W | [7 empty] | ASCII
3016 |  |  | DryContac tFuncEn |  |  |  | Dry Contact function enable | [17 empty] | R/W |  |  | 0/1 | [11 empty] | 0:Disable, 1: Enable
3017 |  |  | DryContac tOnRate |  |  |  | The power rate of dry contact turn on | [17 empty] | R/W |  |  | 0~1000 |  |  |  |  | 0.1%
3018 |  |  | WorkMod e |  |  |  | WorkMode 0:default,1: System Retrofit 2: Multi-Parallel | [17 empty] | R/W |  |  | 0、1、2 | [11 empty] | MIN2.5~6KTL-XH/X A Double CT special
3019 |  |  | DryContac tOffRate |  |  |  | Dry Contact Off Rate, Dry contact closure power | [17 empty] | R/W |  |  | 0~100 |  |  |  |  | 0.1% | [6 empty] | Dry contact closure power percentage
3020 |  |  | BoxCtrlInv Order |  |  |  | Box Ctrl Inv Order | [17 empty] | R/W | [14 empty] | control instruction
3021 |  |  | ExterCom mOffGridE n |  |  |  | External communication setting manual off-network enable | [17 empty] | R/W | [14 empty] | 0x00: Disable; （default） 0x01: Enable;
3022 |  |  | uwBdcSto pWorkOfB usVolt |  |  |  | BdcStopWorkOfBusVolt | [17 empty] | R
3023 |  |  | bGridType |  |  |  | GridType---0:SinglePhase 1:ThreePhase 2:SplitPhase | [17 empty] | R/W |  |  | 0、1、2 | [11 empty] | MIN2.5~6KTL-XH/X A Double CT special
3024 |  |  | Float charge current limit |  |  |  | When charge current battery need is lower than this value, enter into float charge | [17 empty] | R/W | [7 empty] | 0.1A |  |  |  | 600 |  |  | CC current
3025 |  |  | VbatWarni ng |  |  |  | "Battery-low" warning setup voltage | [17 empty] | R/W | [7 empty] | 0.1V |  |  |  | 4800 |  |  | Lead acid battery LV voltage
3026 |  |  | VbatlowW arnClr |  |  |  | "Battery-low" warning clear voltage Clear battery low voltage error voltage point Load Percent (only lead-Acid): 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%); | [17 empty] | R/W | [7 empty] | 0.1V
3027 |  |  | Vbatstopfo rdischarge |  |  |  | Battery cut off voltage Should stop discharge when lower than this voltage(only lead-Acid): 46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%); | [17 empty] | R/W | [7 empty] | 0.1V
3028 |  |  | Vbat stop for charge |  |  |  | Battery over charge volt, Should stop charge when higher than this voltage | [17 empty] | R/W | [7 empty] | 0.01V |  |  |  | 5800
3029 |  |  | Vbat start for discharge |  |  |  | Battery start discharge volt, Should not discharge when lower than this voltage | [17 empty] | R/W | [7 empty] | 0.01V |  |  |  | 4800
3030 |  |  | Vbat constant charge |  |  |  | Battery constant charge voltage,CV voltage（acid） can charge when lower than this voltage | [17 empty] | R/W | [7 empty] | 0.01V |  |  |  | 5800
3031 |  |  | Battemp lower limit d |  |  |  | Battery temperature lower limit for discharge | [17 empty] | R/W |  |  | 0-200,10 00-1400 |  |  |  |  | 0.1℃ |  |  |  | 1170 |  |  | 0-200:0-20℃ 1000-1400:-40-0℃
3032 |  |  | Bat temp upper limit d |  |  |  | Battery temperature upper limit for discharge | [17 empty] | R/W | [7 empty] | 0.1℃ |  |  |  | 420
3033 |  |  | Bat temp lower limit c |  |  |  | Battery temperature lower limit for charge | [17 empty] | R/W |  |  | 0-200,10 00-1400 |  |  |  |  | 0.1℃ |  |  |  | 30 |  |  | 0-200:0-20℃ 1000-1400:-40-0℃
3034 |  |  | Bat temp upper limit c |  |  |  | Battery temperature upper limit for charge | [17 empty] | R/W | [7 empty] | 0.1℃ |  |  |  | 370 |  |  | Battery temperature upper limit
3035 |  |  | uwUnderF reDischarg eDelyTime |  |  |  | Under Fre Delay Time | [17 empty] | R/W | [7 empty] | 50ms | [6 empty] | Under Fre Delay Time
3036 |  |  | GridFirstDi schargePo werRate |  |  |  | Discharge Power Rate when Grid First | [17 empty] | R/W |  |  | 1-255
3037 |  |  | GridFirstSt opSOC |  |  |  | Stop Discharge soc when Grid First | [17 empty] | R/W |  |  | 1-100 | [11 empty] | For US model,Valid in off-grid mode,modified in firmware version ZACA-08/UEAA-09
3038 |  |  | Time 1(xh) |  |  |  | Period 1: [Start Time ~ End Time], [Charge/Discharge], [Disable/Enable] 3038 enable, charge and discharge, start time, end time 3039 | [17 empty] | R/W | [14 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled;
3039 | [24 empty] | R/W | [14 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3040 |  |  | Time 2(xh) |  |  |  | Time period 2: [start time ~ end time], [charge / discharge], [disable / enable] 3040 enable, charge and discharge, start time, 3041 end time | [17 empty] | R/W | [14 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled;
3041 | [24 empty] | R/W | [14 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3042 |  |  | Time 3(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3043 | [24 empty] | R/W | [14 empty] | With Time1
3044 |  |  | Time 4(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3045 | [24 empty] | R/W | [14 empty] | With Time1
3046 |  |  | INVHWVer sion |  |  |  | US inverter hardware version | [17 empty] | R | [7 empty] | ASCII | [6 empty] | V1: 5K off Grid V2: 10K off Grid with dual AC output V3: 10K off Grid, output with a single AC port
3047 |  |  | BatFirstPo werRate |  |  |  | Charge Power Rate when Bat First | [20 empty] | 1-100
3048 |  |  | wBatFirst stop SOC |  |  |  | Stop Charge soc when Bat First | [20 empty] | 1-100
3049 |  |  | AcChargeE nable |  |  |  | AcChargeEnable | [32 empty] | Enable :1 Disable:0
3050 |  |  | Time 5(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3051 | [24 empty] | R/W | [14 empty] | With Time1
3052 |  |  | Time 6(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3053 | [24 empty] | R/W | [14 empty] | With Time1
3054 |  |  | Time 7(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3055 | [24 empty] | R/W | [14 empty] | With Time1
3056 |  |  | Time 8(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3057 | [24 empty] | R/W | [14 empty] | With Time1
3058 |  |  | Time 9(xh) |  |  |  | With Time1 | [17 empty] | R/W | [14 empty] | With Time1
3059 | [24 empty] | R/W | [14 empty] | With Time1
…… |  |  | Reserve
3067 |  |  | OnGridGri dFirstStop SOC |  |  |  | Stop Discharge soc when Grid First and on-grid | [17 empty] | R/W |  |  | 1-100 | [11 empty] | For US model, Valid in off-grid mode,added in firmware version ZACA-08/UEAA-09
…… |  |  | Reserve
3070 |  |  | BatteryTyp e |  |  |  | Battery type choose of buck-boost input | [17 empty] | R/W | [14 empty] | Battery type 0:Lithium 1:Lead-acid 2:other
3071 |  |  | BatMdlSer ia/ParalNu m |  |  |  | BatMdlSeria/ParalNum The upper 8 bits indicate the number of series segments; The lower 8 bits indicate the number of parallel sections; | [17 empty] | R/W | [14 empty] | SPH4-11K used
3072 |  |  | bTurnoffA cEnable |  |  |  | Enable Pre-PTO function | [17 empty] | R/W |  |  | 0/1 | [11 empty] | 1:Enable 0:Disable
3073 |  |  | Generator ChargeEna ble |  |  |  | Enable battery charge from generator function | [17 empty] | R/W |  |  | 0/1 | [11 empty] | 1:Enable 0:Disable
3074 |  |  | Generator OnCmd |  |  |  | Force the generator on,off or not forced [1.27 add] [1.31 Modify] | [17 empty] | R/W |  |  | 0~2 | [11 empty] | 0:Not forced 1:Force generator on 2:Disable Generator
... |  |  | Reserved
3077 |  |  | uwGenera torSpecPo wer |  |  |  | generator rated power | [17 empty] | R/W | [7 empty] | 1W | [6 empty] | For US model,added in firmware version ZAca-31/UEaa-28
3078 |  |  | Reserved
3079 |  |  | UpsFunEn |  |  |  | Ups function enable or disable | [17 empty] | R/W | [11 empty] | 0 |  |  | 0:disable 1:enable
3080 |  |  | UPSVoltSe t |  |  |  | UPS output voltage | [17 empty] | R/W | [11 empty] | 0 |  |  | 0:230V 1:208V 2:240V
3081 |  |  | UPSFreqSe t |  |  |  | UPS output frequency | [17 empty] | R/W | [11 empty] | 0 |  |  | 0:50Hz 1:60Hz
3082 |  |  | bLoadFirst StopSocSe t |  |  |  | StopSoc When LoadFirst | [17 empty] | R/W |  |  | 13-100 | [11 empty] | Ratio Deleted in firmware version ZACA-04/UEAA-04
3082 |  |  | BackUpBo xEnable |  |  |  | BackUp Box Enable | [17 empty] | R/W |  |  | 0/1 | [11 empty] | 0:disable; 1:enable (for XH model,not used in US model,)
|  |  | On-Grid Discharge Stop SOC |  |  |  | Stop Discharge soc when on-grid mode | [17 empty] | R/W |  |  | 1-100 | [11 empty] | For US model, Valid in on-grid mode,same usage as holding 3067, added in firmware version ZACA-09
3083 |  |  | AustraliaR egion |  |  |  | Australian region | [17 empty] | R/W |  |  | 0~3 | [11 empty] | 0:Region A; 1:Region B; 2:Region C; 3:Region NZ;
3084 |  |  | Reserved
3085 |  |  | Com Address |  |  |  | Communication addr | [17 empty] | R/W | [11 empty] | 1 |  |  | 1 :Communication addr=1 1 ~ 254 : Communication addr=1~254
3086 |  |  | BaudRate |  |  |  | Communication BaudRate | [17 empty] | R/W | [11 empty] | 0 |  |  | 0: 9600 bps 1: 38400 bps
3087 |  |  | Serial NO. 1 |  |  |  | Serial Number 1-2 | [17 empty] | R/W | [7 empty] | ASCII | [6 empty] | For battery
3088 |  |  | Serial NO. 2 |  |  |  | Serial Number 3-4 | [17 empty] | R/W | [7 empty] | ASCII
3089 |  |  | Serial NO. 3 |  |  |  | Serial Number 5-6 | [17 empty] | R/W | [7 empty] | ASCII
3090 |  |  | Serial NO. 4 |  |  |  | Serial Number 7-8 | [17 empty] | R/W | [7 empty] | ASCII
3091 |  |  | Serial No. 5 |  |  |  | Serial Number 9-10 | [17 empty] | R/W | [7 empty] | ASCII
3092 |  |  | Serial No.6 |  |  |  | Serial Number 11-12 | [17 empty] | R/W | [7 empty] | ASCII
3093 |  |  | Serial No. 7 |  |  |  | Serial Number 13-14 | [17 empty] | R/W | [7 empty] | ASCII
3094 |  |  | Serial No. 8 |  |  |  | Serial Number 15-16 | [17 empty] | R/W | [7 empty] | ASCII
3095 |  |  | BdcResetC md |  |  |  | BDC Reset command | [17 empty] | R/W | [14 empty] | 0:Invalid data 1:Reset setting parameters 2:Reset correction parameter 3:Clear historical power
3096 |  |  | ARKM3 Code |  |  |  | BDCMonitoring software code | [17 empty] | R | [7 empty] | ASCII | [6 empty] | ZEBA
3097
3098 |  |  | DTC |  |  |  | DTC | [17 empty] | R
3099 |  |  | FW Code |  |  |  | DSP software code | [17 empty] | R | [7 empty] | ASCII
3100
3101 |  |  | Processor1 FW Vision |  |  |  | DSP Software Version | [17 empty] | R | [7 empty] | ASCII
3102 |  |  | BusVoltRef |  |  |  | Minimum BUS voltage for charging and discharging batteries | [17 empty] | R
3103 |  |  | ARKM3Ver |  |  |  | BDC monitoring software version | [17 empty] | R
3104 |  |  | BMS_MCU Version |  |  |  | BMS hardware version information | [17 empty] | R |  |  | 1
3105 |  |  | BMS_FW |  |  |  | BMS software version information | [17 empty] | R |  |  | 1
3106 |  |  | BMS_Info |  |  |  | BMS ManufacturerName | [17 empty] | R |  |  | 1
3107 |  |  | BMSCom mType |  |  |  | BMS Communication interface type: | [17 empty] | R |  |  | 1 | [11 empty] | 0: RS485; 1: CAN;
3108 |  |  | Module 4 |  |  |  | BDCmodel (4) | [17 empty] | R/W |  |  | &*11 | [11 empty] | SxxBxx
3109 |  |  | Module 3 |  |  |  | BDCmodel (3) | [17 empty] | R/W |  |  | &*11 | [11 empty] | DxxTxx
3110 |  |  | Module 2 |  |  |  | BDCmodel (2) | [17 empty] | R/W |  |  | &*11 | [11 empty] | PxxUxx
3111 |  |  | Module 1 |  |  |  | BDCmodel (1) | [17 empty] | R/W |  |  | &*11 | [11 empty] | Mxxxx
3112 |  |  | BDCParalle lNomber |  |  |  | Number of BDC parallel | [17 empty] | R | [14 empty] | [1,5] No parallel, the value is fixed to 1
3113 |  |  | unProtocol Ver |  |  |  | BDC Protocol Version Bit8-bit15:The major version number ranges from 0-256. In principle, it cannot be changed Bit0-bit7:Minor version number [0-256]. | [17 empty] | R | [7 empty] | 1 | [6 empty] | If the protocol is changed, you need to update this version No.
3114 |  |  | uwCertific ationVer |  |  |  | BDC CertificationVer | [17 empty] | R | [7 empty] | 1
3115 |  |  | BDCHardw areVersion |  |  |  | BDC hardware version number | [17 empty] | R
3116 |  |  | BCUSoftw areVer |  |  |  | BCU software code | [17 empty] | R | [7 empty] | ASCII
3117
3118 |  |  | HistoricalF aultNum |  |  |  | Historical fault number | [17 empty] | R | [7 empty] | 1
3119 |  |  | RatedCellC apacity |  |  |  | Cell rated capacity | [17 empty] | R |  |  | 0-60000 |  |  |  |  | 1AH
3120 |  |  | BDCNumA ndBatNum |  |  |  | BDC number and number of battery modules in parallel Bit15 to bit13: indicates the number of the BDC in the range [1-4]. Bit12 to bit10: reserved Bit7~bit0: Parallel number of battery modules range[1,25] | [17 empty] | R | [14 empty] | No parallel connection, fixed at 1 (for APX only)
3121 |  |  | RatedBatC apacity |  |  |  | Battery rated capacity | [17 empty] | R |  |  | 0-65535 | [11 empty] | (for APX only)
…… |  |  | Reserved
3124 |  |  | ClearTime Settings |  |  |  | Clear EMS time settings .Clear holding3125-3238 and holding608 | [17 empty] | W | [14 empty] | 1:Clear EMS time settings
US Machine type Time Set
3125 |  |  | Time Month1 |  |  |  | Use with Time1-9（us） ,Add month time | [17 empty] | R/W | [14 empty] | bit0~3:month_L; bit4~7: month_H bit8, 0:disable 1:enable Bit9~15:reserve
3126 |  |  | Time Month2 |  |  |  | Use with Time10-18（us） ,Add month time | [17 empty] | R/W | [14 empty] | With Time Month1
3127 |  |  | Time Month3 |  |  |  | Use with Time19-27（us） ,Add month time | [17 empty] | R/W | [14 empty] | With Time Month1
3128 |  |  | Time Month4 |  |  |  | Use with Time28-36（us） ,Add month time | [17 empty] | R/W | [14 empty] | With Time Month1
3129 |  |  | Time 1 （us） |  |  |  | time1:[starttime~endtime] | [17 empty] | R/W |  |  | [Charge/ discharg e/count er current], [disable/ enable] | [11 empty] | bit0~6:min; bit7~11:hour; bit12~14, 0:loadfirst; 1:batfirst; 2:gridfirst; 3: anti-reflux bit15, 0:disable; 1:enable;
3130 | [24 empty] | R/W | [14 empty] | bit0~6:min; bit7~11:hour; bit12-13, 0:Weekday 1:Weekend 2:WeeK bit14~15:reserve
3131- 3132 |  |  | Time 2 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3133- 3134 |  |  | Time 3 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3135- 3136 |  |  | Time 4 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3137- 3138 |  |  | Time 5 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3139- 3140 |  |  | Time 6 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3141- 3142 |  |  | Time 7 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3143- 3144 |  |  | Time 8 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3145- 3146 |  |  | Time9（us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3147- 3148 |  |  | Time 10 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3149- 3150 |  |  | Time 11 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3151- 3152 |  |  | Time 12 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3153- 3154 |  |  | Time 13 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3155- 3156 |  |  | Time 14 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3157- 3158 |  |  | Time15 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3159- 3160 |  |  | Time 16 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3161- 3162 |  |  | Time 17 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3163- 3164 |  |  | Time 18 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3165- 3166 |  |  | Time 19 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3167- 3168 |  |  | Time 20 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3169- 3170 |  |  | Time 21 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3171- 3172 |  |  | Time 22 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3173- 3174 |  |  | Time 23 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3175- 3176 |  |  | Time 24 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3177- 3178 |  |  | Time 25 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3179- 3180 |  |  | Time 26 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3181- 3182 |  |  | Time 27 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3183- 3184 |  |  | Time 28 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3185- 3186 |  |  | Time 29 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3187- 3188 |  |  | Time 30 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3189- 3190 |  |  | Time 31 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3191- 3192 |  |  | Time 32 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3193- 3194 |  |  | Time 33 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3195- 3196 |  |  | Time 34 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3197- 3198 |  |  | Time 35 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3199- 3200 |  |  | Time 36 （us） |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Time 1 （us）
3201 |  |  | SpecialDay 1 |  |  |  | SpecialDay1（month,Day） | [17 empty] | R/W | [14 empty] | bit0~7:day; bit8~14:month bit15: 0:disable 1:enable
3202 |  |  | SpecialDay 1_Time1 |  |  |  | Start time | [17 empty] | R/W | [14 empty] | bit0~6:min; bit7~11:hour; bit12~14, 0:loadfirst; 1:batfirst; 2:gridfirst; 3: anti-reflux bit15, 0: disable; 1: enable;
3203 | [6 empty] | endtime | [17 empty] | R/W | [14 empty] | bit0~6:min; bit7~11:hour; bit12~15:reserve
3204- 3205 |  |  | SpecialDay 1_Time2 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3206- 3207 |  |  | SpecialDay 1_Time3 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3208- 3209 |  |  | SpecialDay 1_Time4 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3210- 3211 |  |  | SpecialDay 1_Time5 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3212- 3213 |  |  | SpecialDay 1_Time6 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3214- 3215 |  |  | SpecialDay 1_Time7 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3216- 3217 |  |  | SpecialDay 1_Time8 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3218 ~321 9 |  |  | SpecialDay 1_Time9 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay1_Time 1
3220 |  |  | SpecialDay 2 |  |  |  | SpecialDay2（month,Day） | [17 empty] | R/W | [14 empty] | bit0~7:day; bit8~14:month bit15, 0:disable 1:enable
3221 |  |  | SpecialDay 2_Time1 |  |  |  | Start time | [17 empty] | R/W | [14 empty] | bit0~6: min; bit7~11: hour; bit12~14, 0: loadfirst; 1: batfirst; 2: gridfirst; 3: anti-reflux bit15, 0: disable; 1: enable;
3222 | [6 empty] | endtime | [17 empty] | R/W | [14 empty] | bit0~6: min; bit7~11: hour; bit12~15:reserve
3223 ~322 4 |  |  | SpecialDay 2_Time2 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3225 ~322 6 |  |  | SpecialDay 2_Time3 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3227 ~322 8 |  |  | SpecialDay 2_Time4 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3229 ~323 0 |  |  | SpecialDay 2_Time5 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3231 ~323 2 |  |  | SpecialDay 2_Time6 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3233 ~323 4 |  |  | SpecialDay 2_Time7 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3235 ~323 6 |  |  | SpecialDay 2_Time8 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as SpecialDay2_Time 1
3237 ~323 8 |  |  | SpecialDay 2_Time9 |  |  |  | Same as above | [17 empty] | R/W | [14 empty] | Same as Special Day2_Time1
3239 ~324 9 |  |  | Reserve |  |  |  | Reserve | [17 empty] | R/W
3250 |  |  | bBoxData UploadFla g |  |  |  | Backup box Data Upload Flag | [17 empty] | R | [14 empty] | 0: No 1: Yes
3251 |  |  | uwFirmwa reCode_H |  |  |  | Backup box firmware code | [17 empty] | R | [7 empty] | ASCII
3252 |  |  | uwFirmwa reCode_L | [21 empty] | R | [7 empty] | ASCII
3253 |  |  | ubFirmwar eVersion |  |  |  | Backup box firmware version | [17 empty] | R | [7 empty] | /
3254 |  |  | uwSerialN um0 |  |  |  | Backup box serial number 0 | [17 empty] | R | [7 empty] | ASCII
3255 |  |  | uwSerialN um1 |  |  |  | Backup box serial number 1 | [17 empty] | R | [7 empty] | ASCII
3256 |  |  | uwSerialN um2 |  |  |  | Backup box serial number 2 | [17 empty] | R | [7 empty] | ASCII
3257 |  |  | uwSerialN um3 |  |  |  | Backup box serial number 3 | [17 empty] | R | [7 empty] | ASCII
3258 |  |  | uwSerialN um4 |  |  |  | Backup box serial number 4 | [17 empty] | R | [7 empty] | ASCII
3259 |  |  | uwSerialN um5 |  |  |  | Backup box serial number 5 | [17 empty] | R | [7 empty] | ASCII
3260 |  |  | uwSerialN um6 |  |  |  | Backup box serial number 6 | [17 empty] | R | [7 empty] | ASCII
3261 |  |  | uwSerialN um7 |  |  |  | Backup box serial number 7 | [17 empty] | R | [7 empty] | ASCII
3262 |  |  | uwSerialN um8 |  |  |  | Backup box serial number 8 | [17 empty] | R | [7 empty] | ASCII
3263 |  |  | uwSerialN um9 |  |  |  | Backup box serial number 9 | [17 empty] | R | [7 empty] | ASCII
3264 |  |  | uwSerialN um10 |  |  |  | Backup box serial number 10 | [17 empty] | R | [7 empty] | ASCII
3265 |  |  | uwSerialN um11 |  |  |  | Backup box serial number 11 | [17 empty] | R | [7 empty] | ASCII
3266 |  |  | uwSerialN um12 |  |  |  | Backup box serial number 12 | [17 empty] | R | [7 empty] | ASCII
3267 |  |  | uwSerialN um13 |  |  |  | Backup box serial number 13 | [17 empty] | R | [7 empty] | ASCII
3268 |  |  | uwSerialN um14 |  |  |  | Backup box serial number 14 | [17 empty] | R | [7 empty] | ASCII
3269 |  |  | uwAFCIFir mwareCod e_H |  |  |  | AFCI software code | [17 empty] | R | [7 empty] | ASCII
3270 |  |  | uwAFCIFir mwareCod e_L |  |  |  | AFCI software code | [17 empty] | R | [7 empty] | ASCII
3271 |  |  | uwAFCIFir mwareVer |  |  |  | AFCI software version | [17 empty] | R
3272 |  |  | BusbarPro tectEn |  |  |  | Busbar protect enable | [17 empty] | R/W |  |  | 0/1 | [8 empty] | 0 |  |  | 0:Disable 1:Enable
3273 |  |  | BusbarPro tectCurren t |  |  |  | Busbar protect current | [17 empty] | R/W |  |  | 0-500A |  |  |  |  | 1A |  |  |  | 0
3274 |  |  | BusbarPro tectFailCur rent |  |  |  | Busbar protect current when meter connect error | [17 empty] | R/W |  |  | 0-500A |  |  |  |  | 1A |  |  |  | 0
3275 ~328 1 |  |  | Reserve |  |  |  | Reserve
3282 |  |  | BypassMo deEnterEn |  |  |  | Bypass mode enter enable | [17 empty] | R/W |  |  | 0/1 | [8 empty] | 0 |  |  | 0:Disable 1:Enable
BDC information (support up to 10 parallel BDC)
5000-5039 | [6 empty] | 1 | [25 empty] | Reference 3085 to 3124 for a total of 40 registers Description
5040-5079 | [6 empty] | 2
5000+(N-1)*40--- 5039+(N-1)*40 | [6 empty] | N
Battery module information (support up to 64 parallel BDC)（Special for APX）
5400 |  |  | Serial NO. 1 | [5 empty] | Serial Number 1-2 | [15 empty] | R | [7 empty] | ASCII | [6 empty] | For battery module
5401 |  |  | Serial NO. 2 | [5 empty] | Serial Number 3-4 | [15 empty] | R | [7 empty] | ASCII
5402 |  |  | Serial NO. 3 | [5 empty] | Serial Number 5-6 | [15 empty] | R | [7 empty] | ASCII
5403 |  |  | Serial NO. 4 | [5 empty] | Serial Number 7-8 | [15 empty] | R | [7 empty] | ASCII
5404 |  |  | Serial No. 5 | [5 empty] | Serial Number 9-10 | [15 empty] | R | [7 empty] | ASCII
5405 |  |  | Serial No.6 | [5 empty] | Serial Number 11-12 | [15 empty] | R | [7 empty] | ASCII
5406 |  |  | Serial No. 7 | [5 empty] | Serial Number 13-14 | [15 empty] | R | [7 empty] | ASCII
5407 |  |  | Serial No. 8 | [5 empty] | Serial Number 15-16 | [15 empty] | R | [7 empty] | ASCII
5408 |  |  | BatDSPCode | [5 empty] | DSP software code | [15 empty] | R | [7 empty] | ASCII | [6 empty] | WAAA
5409
5410 |  |  | BatDSPVersio n | [5 empty] | DSP version number | [15 empty] | R
5411 |  |  | BatMCUCode | [5 empty] | Monitoring software code | [15 empty] | R | [7 empty] | ASCII | [6 empty] | QABA
5412
5413 |  |  | BatMCUVersi on | [5 empty] | Monitoring version number | [15 empty] | R
5414 |  |  | BatManufact urerInfor | [5 empty] | Manufacturer information | [15 empty] | R | [9 empty] | Bit15~bit 12: Cell model Bit11~bit 8: Battery manufact urers Bit7~bit4: Pack Foundry Bit3~bit0: hardware version number |  |  |  |  | Bit15~bit12: 0: Invalid value 1: Li-iron_50AH 2:Ternary_50AH Bit11~bit8: 0: Invalid value 1: Rept 2:EVE 3:BYD 4:ATL 5:CATL Bit7~bit4: 0:Growatt 1: Desay Bit3~bit0: 0-15
5415 |  |  | BatNumber | [5 empty] | Number of the battery module | [15 empty] | R | [14 empty] | Bit15~bit13: Indicates the number of the BDC group where the battery is located, range [1-4] Bit12~bit8: indicates the serial number of the battery module in the BDC group, range [1-21] Bit7~bit0: Reserved
5416 |  |  | SOX firmware version | [21 empty] | R
5417 |  |  | PowerCmd | [5 empty] | Power on and off command | [15 empty] | R | [14 empty] | 0: standby 1: operation 2: invalid 3: shutdown
5418 |  |  | MaxPowerPe cnent | [5 empty] | Maximum charge and discharge power percentage | [15 empty] | R | [7 empty] | 1% | [6 empty] | Bit15~bit8: Percentage of maximum discharge power, range [0-128] Bit7~bit0: Percentage of maximum secondary power, range [0-100]
5419 |  |  | SOCLimit | [5 empty] | Charge and discharge SOC limit | [15 empty] | R | [7 empty] | 1% | [6 empty] | Bit15~bit8: discharge SOC limit, range [10-100] Bit7~bit0: charging SOC limit, range [0-100]
…… |  |  | Reserved
5440-5479 | [8 empty] | Battery module 2 | [23 empty] | Reference 5400 to 5439 for a total of 40 registers description
5480-5519 | [8 empty] | Battery module 3 | [23 empty] | Reference 5400 to 5439 for a total of 40 registers description
5400+(N-1)*40---- 5439+(N-1)*40 | [8 empty] | Battery module N(supports up to 64 battery modules)
BDC information (support up to 10 parallel BDC)
7960 |  |  | uwSerialNum0 | [7 empty] | BDC1 new serial number 0 | [13 empty] | R |  |  |  | ASCII
7961 |  |  | uwSerialNum1 | [7 empty] | BDC1 new serial number 1 | [13 empty] | R |  |  |  | ASCII
7962 |  |  | uwSerialNum2 | [7 empty] | BDC1 new serial number 2 | [13 empty] | R |  |  |  | ASCII
7963 |  |  | uwSerialNum3 | [7 empty] | BDC1 new serial number 3 | [13 empty] | R |  |  |  | ASCII
7964 |  |  | uwSerialNum4 | [7 empty] | BDC1 new serial number 4 | [13 empty] | R |  |  |  | ASCII
7965 |  |  | uwSerialNum5 | [7 empty] | BDC1 new serial number 5 | [13 empty] | R |  |  |  | ASCII
7966 |  |  | uwSerialNum6 | [7 empty] | BDC1 new serial number 6 | [13 empty] | R |  |  |  | ASCII
7967 |  |  | uwSerialNum7 | [7 empty] | BDC1 new serial number 7 | [13 empty] | R |  |  |  | ASCII
7968 |  |  | uwSerialNum8 | [7 empty] | BDC1 new serial number | [13 empty] | R |  |  |  | ASCII
7969 |  |  | uwSerialNum9 | [7 empty] | BDC1 new serial number 9 | [13 empty] | R |  |  |  | ASCII
7970 |  |  | uwSerialNum10 | [7 empty] | BDC1 new serial number 10 | [13 empty] | R |  |  |  | ASCII
7971 |  |  | uwSerialNum11 | [7 empty] | BDC1 new serial number 11 | [13 empty] | R |  |  |  | ASCII
7972 |  |  | uwSerialNum12 | [7 empty] | BDC1 new serial number 12 | [13 empty] | R |  |  |  | ASCII
7973 |  |  | uwSerialNum13 | [7 empty] | BDC1 new serial number 13 | [13 empty] | R |  |  |  | ASCII
7974 |  |  | uwSerialNum14 | [7 empty] | BDC1 new serial number 14 | [13 empty] | R |  |  |  | ASCII
…… | [10 empty] | reserve
BDC information (support up to 10 parallel BDC)
8020~8079 | [10 empty] | 2 | [21 empty] | Reference 7960 to 8019 for a total of 60 registers Description
8080~8139 | [10 empty] | 3
7960+(N-1)*60~8019+ (N-1)*60 | [10 empty] | N
Battery module information (support up to 64 parallel BDC)（Special for APX）
8560 |  |  | uwSerialNum0 | [7 empty] | Battery module 1 new serial number 0 | [13 empty] | R |  |  |  | ASCII
8561 |  |  | uwSerialNum1 | [7 empty] | Battery module 1 new serial number 1 | [13 empty] | R |  |  |  | ASCII
8562 |  |  | uwSerialNum2 | [7 empty] | Battery module 1 new serial number 2 | [13 empty] | R |  |  |  | ASCII
8563 |  |  | uwSerialNum3 | [7 empty] | Battery module 1 new serial number 3 | [13 empty] | R |  |  |  | ASCII
8564 |  |  | uwSerialNum4 | [7 empty] | Battery module 1 new serial number 4 | [13 empty] | R |  |  |  | ASCII
8565 |  |  | uwSerialNum5 | [7 empty] | Battery module 1 new serial number 5 | [13 empty] | R |  |  |  | ASCII
8566 |  |  | uwSerialNum6 | [7 empty] | Battery module 1 new serial number 6 | [13 empty] | R |  |  |  | ASCII
8567 |  |  |  | uwSerialNum7 | [7 empty] | Battery module 1 new serial number 7 | [13 empty] | R |  |  | ASCII
8568 |  |  |  | uwSerialNum8 | [7 empty] | Battery module 1 new serial number 8 | [13 empty] | R |  |  | ASCII
8569 |  |  |  | uwSerialNum9 | [7 empty] | Battery module 1 new serial number 9 | [13 empty] | R |  |  | ASCII
8570 |  |  |  | uwSerialNum10 | [7 empty] | Battery module 1 new serial number 10 | [13 empty] | R |  |  | ASCII
8571 |  |  |  | uwSerialNum11 | [7 empty] | Battery module 1 new serial number 11 | [13 empty] | R |  |  | ASCII
8572 |  |  |  | uwSerialNum12 | [7 empty] | Battery module 1 new serial number 12 | [13 empty] | R |  |  | ASCII
8573 |  |  |  | uwSerialNum13 | [7 empty] | Battery module 1 new serial number 13 | [13 empty] | R |  |  | ASCII
8574 |  |  |  | uwSerialNum14 | [7 empty] | Battery module 1 new serial number 14 | [13 empty] | R |  |  | ASCII
Battery module information (support up to 64 parallel BDC)（Special for APX）
8575-8589 | [11 empty] | Battery module 2 new serial number | [21 empty] | Reference 8560 to 8574 for a total of 15 registers Description Each BDC is allowed to connect up to 6 battery modules. So BDC1's battery module SN is from 8560-8650(8560+15*6) BDC2's battery module SN is from 8650-8740(8650+15*6)
8560+(N-1)*15---8574 +(N-1)*15 | [11 empty] | Battery module N new serial number | [21 empty] | Same as above
2.2 Input register
NO. |  |  |  | Variable Name | [8 empty] | Description | [18 empty] | Range | [5 empty] | Unit |  |  |  | Note
First group
0 |  |  |  | Inverter Status | [8 empty] | Inverter run state | [18 empty] | 0:waiting , 1:normal , 3:fault
1 |  |  |  | Ppv H | [8 empty] | Input power (high) | [24 empty] | 0.1W
2 |  |  |  | Ppv L | [8 empty] | Input power (low) | [24 empty] | 0.1W
3 |  |  |  |  | Vpv1 | [7 empty] | PV1 voltage | [24 empty] | 0.1V
4 |  |  |  |  | PV1Curr | [7 empty] | PV1 input current | [24 empty] | 0.1A
5 |  |  |  |  | Ppv1 H | [7 empty] | PV1 input power(high) | [24 empty] | 0.1W
6 |  |  |  |  | Ppv1 L | [7 empty] | PV1 input power(low) | [24 empty] | 0.1W
7 |  |  |  |  | Vpv2 | [7 empty] | PV2 voltage | [24 empty] | 0.1V
8 |  |  |  |  | PV2Curr | [7 empty] | PV2 input current | [24 empty] | 0.1A
9 |  |  |  |  | Ppv2 H | [7 empty] | PV2 input power (high) | [24 empty] | 0.1W
10 |  |  |  |  | Ppv2 L | [7 empty] | PV2 input power (low) | [24 empty] | 0.1W
11 |  |  |  |  | Vpv3 | [7 empty] | PV3 voltage | [24 empty] | 0.1V
12 |  |  |  |  | PV3Curr | [7 empty] | PV3 input current | [24 empty] | 0.1A
13 |  |  |  |  | Ppv3 H | [7 empty] | PV3 input power (high) | [24 empty] | 0.1W
14 |  |  |  |  | Ppv3 L | [7 empty] | PV3 input power (low) | [24 empty] | 0.1W
15 |  |  |  |  | Vpv4 | [7 empty] | PV4 voltage | [24 empty] | 0.1V
16 |  |  |  |  | PV4Curr | [7 empty] | PV4 input current | [24 empty] | 0.1A
17 |  |  |  |  | Ppv4 H | [7 empty] | PV4 input power (high) | [24 empty] | 0.1W
18 |  |  |  |  | Ppv4 L | [7 empty] | PV4 input power (low) | [24 empty] | 0.1W
19 |  |  |  |  | Vpv5 | [7 empty] | PV5 voltage | [24 empty] | 0.1V
20 |  |  |  |  | PV5Curr | [7 empty] | PV5 input current | [24 empty] | 0.1A
21 |  |  |  |  | Ppv5H | [7 empty] | PV5 input power(high) | [24 empty] | 0.1W
22 |  |  |  |  | Ppv5 L | [7 empty] | PV5 input power(low) | [24 empty] | 0.1W
23 |  |  |  |  | Vpv6 | [7 empty] | PV6 voltage | [24 empty] | 0.1V
24 |  |  |  |  | PV6Curr | [7 empty] | PV6 input current | [24 empty] | 0.1A
25 |  |  |  |  | Ppv6 H | [7 empty] | PV6 input power (high) | [24 empty] | 0.1W
26 |  |  |  |  | Ppv6 L | [7 empty] | PV6 input power (low) | [24 empty] | 0.1W
27 |  |  |  |  | Vpv7 | [7 empty] | PV7 voltage | [24 empty] | 0.1V
28 |  |  |  |  | PV7Curr | [7 empty] | PV7 input current | [24 empty] | 0.1A
29 |  |  |  |  | Ppv7 H | [7 empty] | PV7 input power (high) | [24 empty] | 0.1W
30 |  |  |  |  | Ppv7 L | [7 empty] | PV7 input power (low) | [24 empty] | 0.1W
31 |  |  |  |  | Vpv8 | [7 empty] | PV8 voltage | [24 empty] | 0.1V
32 |  |  |  |  | PV8Curr | [7 empty] | PV8 input current | [24 empty] | 0.1A
33 |  |  |  |  | Ppv8 H | [7 empty] | PV8 input power (high) | [24 empty] | 0.1W
34 |  |  |  |  | Ppv8 L | [7 empty] | PV8 input power (low) | [24 empty] | 0.1W
35 |  |  |  |  | Pac H | [7 empty] | Output power (high) | [24 empty] | 0.1W
36 |  |  |  |  | Pac L | [7 empty] | Output power (low) | [24 empty] | 0.1W
37 |  |  |  |  | Fac | [7 empty] | Grid frequency | [24 empty] | 0.01Hz
38 |  |  |  |  | Vac1 | [7 empty] | Three/single phase grid voltage | [24 empty] | 0.1V
39 |  |  |  |  | Iac1 | [7 empty] | Three/single phase grid output current | [24 empty] | 0.1A
40 |  |  |  |  | Pac1 H | [7 empty] | Three/single phase grid output watt VA (high) | [24 empty] | 0.1VA
41 |  |  |  |  | Pac1 L | [7 empty] | Three/single phase grid output watt VA(low) | [24 empty] | 0.1VA
42 |  |  |  |  | Vac2 | [7 empty] | Three phase grid voltage | [24 empty] | 0.1V
43 |  |  |  |  | Iac2 | [7 empty] | Three phase grid output current | [24 empty] | 0.1A
44 |  |  |  |  | Pac2 H | [7 empty] | Three phase grid output power (high) | [24 empty] | 0.1VA
45 |  |  |  |  | Pac2 L | [7 empty] | Three phase grid output power (low) | [24 empty] | 0.1VA
46 |  |  |  |  | Vac3 | [7 empty] | Three phase grid voltage | [24 empty] | 0.1V
47 |  |  |  |  | Iac3 | [7 empty] | Three phase grid output current | [24 empty] | 0.1A
48 |  |  |  |  | Pac3 H | [7 empty] | Three phase grid output power (high) | [24 empty] | 0.1VA
49 |  |  |  |  | Pac3 L | [7 empty] | Three phase grid output power (low) | [24 empty] | 0.1VA
50 |  |  |  |  | Vac_RS | [7 empty] | Three phase grid voltage | [24 empty] | 0.1V |  |  |  | Line voltage
51 |  |  |  |  | Vac_ST | [7 empty] | Three phase grid voltage | [24 empty] | 0.1V |  |  |  | Line voltage
52 |  |  |  |  | Vac_TR | [7 empty] | Three phase grid voltage | [24 empty] | 0.1V |  |  |  | Line voltage
53 |  |  |  |  | Eactoday H | [7 empty] | Today generate energy (high) | [24 empty] | 0.1kWH
54 |  |  |  |  | Eac today L | [7 empty] | Today generate energy (low) | [24 empty] | 0.1kWH
55 |  |  |  |  | Eac total H | [7 empty] | Total generate energy (high) | [24 empty] | 0.1kWH
56 |  |  |  |  | Eac total L | [7 empty] | Total generate energy (low) | [24 empty] | 0.1kWH
57 |  |  |  |  | Time total H | [7 empty] | Work time total (high) | [24 empty] | 0.5s
58 |  |  |  |  | Time total L | [7 empty] | Work time total (low) | [24 empty] | 0.5s
59 |  |  |  |  | Epv1_today H | [7 empty] | PV1Energy today(high) | [24 empty] | 0.1kWh
60 |  |  |  |  | Epv1_today L | [7 empty] | PV1Energy today (low) | [24 empty] | 0.1kWh
61 |  |  |  |  | Epv1_total H | [7 empty] | PV1Energy total(high) | [24 empty] | 0.1kWh
62 |  |  |  |  | Epv1_total L | [7 empty] | PV1Energy total (low) | [24 empty] | 0.1kWh
63 |  |  |  |  | Epv2_today H | [7 empty] | PV2Energy today(high) | [24 empty] | 0.1kWh
64 |  |  |  |  | Epv2_today L | [7 empty] | PV2Energy today (low) | [24 empty] | 0.1kWh
65 |  |  |  |  | Epv2_total H | [7 empty] | PV2Energy total(high) | [24 empty] | 0.1kWh
66 |  |  |  |  | Epv2_total L | [7 empty] | PV2Energy total (low) | [24 empty] | 0.1kWh
67 |  |  |  |  | Epv3_today H | [7 empty] | PV3 Energy today(high) | [24 empty] | 0.1kWh
68 |  |  |  |  | Epv3_today L | [7 empty] | PV3 Energy today (low) | [24 empty] | 0.1kWh
69 |  |  |  |  | Epv3_total H | [7 empty] | PV3 Energy total(high) | [24 empty] | 0.1kWh
70 |  |  |  |  | Epv3_total L | [7 empty] | PV3 Energy total (low) | [24 empty] | 0.1kWh
71 |  |  |  |  | Epv4_today H | [7 empty] | PV4Energy today(high) | [24 empty] | 0.1kWh
72 |  |  |  |  | Epv4_today L | [7 empty] | PV4Energy today (low) | [24 empty] | 0.1kWh
73 |  |  |  |  | Epv4_total H | [7 empty] | PV4Energy total(high) | [24 empty] | 0.1kWh
74 |  |  |  |  | Epv4_total L | [7 empty] | PV4Energy total (low) | [24 empty] | 0.1kWh
75 |  |  |  |  | Epv5_today H | [7 empty] | PV5Energy today(high) | [24 empty] | 0.1kWh
76 |  |  |  |  | Epv5_today L | [7 empty] | PV5Energy today (low) | [24 empty] | 0.1kWh
77 |  |  |  |  | Epv5_total H | [7 empty] | PV5Energy total(high) | [24 empty] | 0.1kWh
78 |  |  |  |  | Epv5_total L | [7 empty] | PV5Energy total (low) | [24 empty] | 0.1kWh
79 |  |  |  |  | Epv6_today H | [7 empty] | PV6Energy today(high) | [24 empty] | 0.1kWh
80 |  |  |  |  | Epv6_today L | [7 empty] | PV6Energy today (low) | [24 empty] | 0.1kWh
81 |  |  |  |  | Epv6_total H | [7 empty] | PV6Energy total(high) | [24 empty] | 0.1kWh
82 |  |  |  |  | Epv6_total L | [7 empty] | PV6Energy total (low) | [24 empty] | 0.1kWh
83 |  |  |  |  | Epv7_today H | [7 empty] | PV7Energy today(high) | [24 empty] | 0.1kWh
84 |  |  |  |  | Epv7_today L | [7 empty] | PV7Energy today (low) | [24 empty] | 0.1kWh
85 |  |  |  |  | Epv7_total H | [7 empty] | PV7 Energy total(high) | [24 empty] | 0.1kWh
86 |  |  |  |  | Epv7_total L | [7 empty] | PV7Energy total (low) | [24 empty] | 0.1kWh
87 |  |  |  |  | Epv8_today H | [7 empty] | PV8Energy today(high) | [24 empty] | 0.1kWh
88 |  |  |  |  | Epv8_today L | [7 empty] | PV8Energy today (low) | [24 empty] | 0.1kWh
89 |  |  |  |  | Epv8_total H | [7 empty] | PV8Energy total(high) | [24 empty] | 0.1kWh
90 |  |  |  |  | Epv8_total L | [7 empty] | PV8Energy total (low) | [24 empty] | 0.1kWh
91 |  |  |  |  | Epv_total H | [7 empty] | PV Energy total(high) | [24 empty] | 0.1kWh
92 |  |  |  |  | Epv_total L | [7 empty] | PV Energy total (low) | [24 empty] | 0.1kWh
93 |  |  |  |  | Temp1 | [7 empty] | Inverter temperature | [24 empty] | 0.1C
94 |  |  |  |  | Temp2 | [7 empty] | The inside IPM in inverter Temper-ature | [24 empty] | 0.1C
95 |  |  |  |  | Temp3 | [7 empty] | Boost temperature | [24 empty] | 0.1C
96 |  |  |  |  | Temp4 | [36 empty] | reserved
97 |  |  |  |  | uwBatVolt_DSP | [7 empty] | BatVolt_DSP | [24 empty] | 0.1V |  |  |  | BatVolt(DSP )
98 |  |  |  |  | P Bus Voltage | [7 empty] | P Bus inside Voltage | [24 empty] | 0.1V
99 |  |  |  |  | N Bus Voltage | [7 empty] | N Bus inside Voltage | [24 empty] | 0.1V
100 |  |  |  |  | IPF | [7 empty] | Inverter output PF now | [18 empty] | 0-20000
101 |  |  |  |  | RealOPPercent | [7 empty] | Real Output power Percent | [24 empty] | 1%
102 |  |  |  |  | OPFullwatt H | [7 empty] | Output Maxpower Limited high
103 |  |  |  |  | OPFullwatt L | [7 empty] | Output Maxpower Limited low | [24 empty] | 0.1W
104 |  |  |  |  | DeratingMode | [7 empty] | DeratingMode | [28 empty] | 0:no derate 1:PV 2:* 3:Vac 4:Fac 5:Tboost 6:Tinv 7:Control 8:* 9:*OverBack ByTime
105 |  |  |  |  | Fault Maincode | [7 empty] | Inverter fault maincode
106 |  |  |  |  | Reserve
107 |  |  |  |  | Fault Subcode | [7 empty] | Inverter fault subcode
108 |  |  |  |  | RemoteCtrlEn | [7 empty] | Remote Control Enable | [18 empty] | 0.Load First 1.BatFirst 2.Grid | [9 empty] | StoragePow er (SPA)
109 |  |  |  |  | RemoteCtrlPow er | [7 empty] | Remote Control Power | [28 empty] | StoragePow er (SPA)
110 |  |  |  |  | Warning bit H | [7 empty] | Warning bit H
111 |  |  |  |  | Warn Subcode | [7 empty] | Inverter warn subcode
112 |  |  |  |  | Warn Maincode | [7 empty] | Inverter warn maincode
[5 empty] | EACharge_Toda y_H | [7 empty] | ACCharge energy today | [24 empty] | 0.1kwh |  |  |  | Storage Power
113 |  |  |  |  | real Power Percent | [7 empty] | real Power Percent | [18 empty] | 0-100 | [5 empty] | % |  |  |  | MAX
[5 empty] | EACharge_Toda y_L | [7 empty] | ACCharge energy today | [24 empty] | 0.1kwh |  |  |  | Storage Power
114 |  |  |  |  | inv start delay time | [7 empty] | inv start delay time | [28 empty] | MAX
[5 empty] | EACharge_Total _H | [7 empty] | ACCharge energy total | [24 empty] | 0.1kwh |  |  |  | Storage Power
115 |  |  |  |  | bINVAllFaultCo de | [7 empty] | bINVAllFaultCode | [28 empty] | MAX
[5 empty] | EACharge_Total _L | [7 empty] | ACCharge energy total | [24 empty] | 0.1kwh |  |  |  | Storage Power
116 |  |  |  |  | AC charge Power_H | [7 empty] | Grid power to local load | [24 empty] | 0.1kwh |  |  |  | Storage Power
117 |  |  |  |  | AC charge Power_L | [7 empty] | Grid power to local load | [24 empty] | 0.1kwh |  |  |  | Storage Power
118 |  |  |  |  | Priority | [7 empty] | 0:Load First 1:Battery First 2:Grid First | [28 empty] | Storage Power
119 |  |  |  |  | Battery Type | [7 empty] | 0:Lead-acid 1:Lithium battery | [28 empty] | Storage Power
120 |  |  |  |  | AutoProofread CMD | [7 empty] | Aging mode Auto-calibration command | [28 empty] | Storage Power
… |  |  |  |  | reserved | [36 empty] | reserved
124 |  |  |  |  | reserved | [36 empty] | reserved
Second group
125 |  |  |  |  | PID PV1+ Voltage | [7 empty] | PID PV1PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
126 |  |  |  |  | PID PV1+ Current | [7 empty] | PID PV1PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
127 |  |  |  |  | PID PV2+ Voltage | [7 empty] | PID PV2PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
128 |  |  |  |  | PID PV2+ Current | [7 empty] | PID PV2PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
129 |  |  |  |  | PID PV3+ Voltage | [7 empty] | PID PV3PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
130 |  |  |  |  | PID PV3+ Current | [7 empty] | PID PV3PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
131 |  |  |  |  | PID PV4+ Voltage | [7 empty] | PID PV4PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
132 |  |  |  |  | PID PV4+ Current | [7 empty] | PID PV4PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
133 |  |  |  |  | PID PV5+ Voltage | [7 empty] | PID PV5PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
134 |  |  |  |  | PID PV5+ Current | [7 empty] | PID PV5PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
135 |  |  |  |  | PID PV6+ Voltage | [7 empty] | PID PV6PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
136 |  |  |  |  | PID PV6+ Current | [7 empty] | PID PV6PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
137 |  |  |  |  | PID PV7+ Voltage | [7 empty] | PID PV7PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
138 |  |  |  |  | PID PV7+ Current | [7 empty] | PID PV7PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
139 |  |  |  |  | PID PV8+ Voltage | [7 empty] | PID PV8PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
140 |  |  |  |  | PID PV8+ Current | [7 empty] | PID PV8PE Curr | [18 empty] | -10~10m A | [5 empty] | 0.1mA
141 |  |  |  |  | PID Status | [7 empty] | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | [18 empty] | 0~3
142 |  |  |  |  | V _String1 | [7 empty] | PV String1 voltage | [24 empty] | 0.1V
143 |  |  |  |  | Curr _String1 | [7 empty] | PV String1 current | [18 empty] | -15~15A | [5 empty] | 0.1A
144 |  |  |  |  | V _String2 | [7 empty] | PV String2 voltage | [24 empty] | 0.1V
145 |  |  |  |  | Curr _String2 | [7 empty] | PV String2 current | [18 empty] | -15~15A | [5 empty] | 0.1A
146 |  |  |  |  | V _String3 | [7 empty] | PV String3 voltage | [24 empty] | 0.1V
147 |  |  |  |  | Curr _String3 | [7 empty] | PV String3 current | [18 empty] | -15~15A | [5 empty] | 0.1A
148 |  |  |  |  | V _String4 | [7 empty] | PV String4 voltage | [24 empty] | 0.1V
149 |  |  |  |  | Curr _String4 | [7 empty] | PV String4 current | [18 empty] | -15~15A | [5 empty] | 0.1A
150 |  |  |  |  | V _String5 | [7 empty] | PV String5 voltage | [24 empty] | 0.1V
151 |  |  |  |  | Curr _String5 | [7 empty] | PV String5 current | [18 empty] | -15~15A | [5 empty] | 0.1A
152 |  |  |  |  | V _String6 | [7 empty] | PV String6 voltage | [24 empty] | 0.1V
153 |  |  |  |  | Curr _String6 | [7 empty] | PV String6 current | [18 empty] | -15~15A | [5 empty] | 0.1A
154 |  |  |  |  | V _String7 | [7 empty] | PV String7 voltage | [24 empty] | 0.1V
155 |  |  |  |  | Curr _String7 | [7 empty] | PV String7 current | [18 empty] | -15~15A | [5 empty] | 0.1A
156 |  |  |  |  | V _String8 | [7 empty] | PV String8 voltage | [24 empty] | 0.1V
157 |  |  |  |  | Curr _String8 | [7 empty] | PV String8 current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
158 |  |  |  |  | V _String9 | [7 empty] | PV String9 voltage | [24 empty] | 0.1V
159 |  |  |  |  | Curr _String9 | [7 empty] | PV String9 current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
160 |  |  |  |  | V _String10 | [7 empty] | PV String10 voltage | [24 empty] | 0.1V
161 |  |  |  |  | Curr _String10 | [7 empty] | PV String10 current | [18 empty] | -15~15A | [5 empty] | 0.1A
162 |  |  |  |  | V _String11 | [7 empty] | PV String11 voltage | [24 empty] | 0.1V
163 |  |  |  |  | Curr _String11 | [7 empty] | PV String11 current | [18 empty] | -15~15A | [5 empty] | 0.1A
164 |  |  |  |  | V _String12 | [7 empty] | PV String12 voltage | [24 empty] | 0.1V
165 |  |  |  |  | Curr _String12 | [7 empty] | PV String12 current | [18 empty] | -15~15A | [5 empty] | 0.1A
166 |  |  |  |  | V _String13 | [7 empty] | PV String13 voltage | [24 empty] | 0.1V
167 |  |  |  |  | Curr _String13 | [7 empty] | PV String13 current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
168 |  |  |  |  | V _String14 | [7 empty] | PV String14 voltage | [24 empty] | 0.1V
169 |  |  |  |  | Curr _String14 | [7 empty] | PV String14 current | [18 empty] | -15~15A | [5 empty] | 0.1A
170 |  |  |  |  | V _String15 | [7 empty] | PV String15 voltage | [24 empty] | 0.1V
171 |  |  |  |  | Curr _String15 | [7 empty] | PV String15 current | [18 empty] | -15~15A | [5 empty] | 0.1A
172 |  |  |  |  | V _String16 | [7 empty] | PV String16 voltage | [24 empty] | 0.1V
173 |  |  |  |  | Curr _String16 | [7 empty] | PV String16 current | [18 empty] | -15~15A | [5 empty] | 0.1A
174 |  |  |  |  | StrUnmatch | [7 empty] | Bit0~15: String1~16 unmatch | [28 empty] | suggestive
175 |  |  |  |  | StrCurrentUnbl ance | [7 empty] | Bit0~15: String1~16 current unblance | [28 empty] | suggestive
176 |  |  |  |  | StrDisconnect | [7 empty] | Bit0~15: String1~16 disconnect | [28 empty] | suggestive
177 |  |  |  |  | PIDFaultCode | [7 empty] | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved
178 |  |  |  |  | String Prompt | [7 empty] | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance Bit3~15:reserved
179 |  |  |  |  | PVWarningValu e | [7 empty] | PV Warning Value
180 |  |  |  |  | DSP075 Warning Value | [7 empty] | DSP075 Warning Value
181 |  |  |  |  | DSP075 Fault Value | [7 empty] | DSP075 Fault Value
182 |  |  |  |  | DSP067 Debug Data1 | [7 empty] | DSP067 Debug Data1
183 |  |  |  |  | DSP067 Debug Data2 | [7 empty] | DSP067 Debug Data2
184 |  |  |  |  | DSP067 Debug Data3 | [7 empty] | DSP067 Debug Data3
185 |  |  |  |  | DSP067 Debug Data4 | [7 empty] | DSP067 Debug Data4
186 |  |  |  |  | DSP067 Debug Data5 | [7 empty] | DSP067 Debug Data5
187 |  |  |  |  | DSP067 Debug Data6 | [7 empty] | DSP067 Debug Data6
188 |  |  |  |  | DSP067 Debug Data7 | [7 empty] | DSP067 Debug Data7
189 |  |  |  |  | DSP067 Debug Data8 | [7 empty] | DSP067 Debug Data8
190 |  |  |  |  | DSP075 Debug Data1 | [7 empty] | DSP075 Debug Data1
191 |  |  |  |  | DSP075 Debug Data2 | [7 empty] | DSP075 Debug Data2
192 |  |  |  |  | DSP075 Debug Data3 | [7 empty] | DSP075 Debug Data3
193 |  |  |  |  | DSP075 Debug Data4 | [7 empty] | DSP075 Debug Data4
194 |  |  |  |  | DSP075 Debug Data55 | [7 empty] | DSP075 Debug Data5
195 |  |  |  |  | DSP075 Debug Data6 | [7 empty] | DSP075 Debug Data6
196 |  |  |  |  | DSP075 Debug Data7 | [7 empty] | DSP075 Debug Data7
197 |  |  |  |  | DSP075 Debug Data8 | [7 empty] | DSP075 Debug Data8
198 |  |  |  |  | bUSBAgingTest OkFlag | [7 empty] | USBAgingTestOkFlag | [18 empty] | 0-1
199 |  |  |  |  | bFlashEraseAgi ngOkFlag | [7 empty] | FlashEraseAgingOkFlag | [18 empty] | 0-1
200 |  |  |  |  | PVISO | [7 empty] | PVISOValue | [24 empty] | KΩ
201 |  |  |  |  | R_DCI | [7 empty] | R DCI Curr | [24 empty] | 0.1mA
202 |  |  |  |  | S_DCI | [7 empty] | S DCI Curr | [24 empty] | 0.1mA
203 |  |  |  |  | T_DCI | [7 empty] | T DCI Curr | [24 empty] | 0.1mA
204 |  |  |  |  | PID_Bus | [7 empty] | PIDBusVolt | [24 empty] | 0.1V
205 |  |  |  |  | GFCI | [7 empty] | GFCI Curr | [24 empty] | mA
206 |  |  |  |  | SVG/APF Status+SVGAPF EqualRatio | [7 empty] | SVG/APF Status+SVGAPFEqualRatio | [18 empty] | 0:None 1:SVG run 2:APF run 3:SVG/AP F Run | [9 empty] | high 8bit: SVG/APF Equal Ratio low 8 bit: SVG/APF Status
207 |  |  |  |  | CT_I _R | [7 empty] | R phase load side current for SVG | [24 empty] | 0.1A
208 |  |  |  |  | CT_I _S | [7 empty] | S phase load side current for SVG | [24 empty] | 0.1A
209 |  |  |  |  | CT_I _T | [7 empty] | T phase load side current for SVG | [24 empty] | 0.1A
210 |  |  |  |  | CT_Q _R H | [7 empty] | R phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
211 |  |  |  |  | CT_Q _R L | [7 empty] | R phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
212 |  |  |  |  | CT_Q _S H | [7 empty] | S phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
213 |  |  |  |  | CT_Q _S L | [7 empty] | S phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
214 |  |  |  |  | CT_Q _T H | [7 empty] | T phase load side output reactive power for SVG(High) | [24 empty] | 0.1Var
215 |  |  |  |  | CT_Q _T L | [7 empty] | T phase load side output reactive power for SVG(low) | [24 empty] | 0.1Var
216 |  |  |  |  | CT HAR_I_R | [7 empty] | R phase load side harmonic | [24 empty] | 0.1A
217 |  |  |  |  | CT HAR_I_S | [7 empty] | S phase load side harmonic | [24 empty] | 0.1A
218 |  |  |  |  | CT HAR_I_T | [7 empty] | T phase load side harmonic | [24 empty] | 0.1A
219 |  |  |  |  | COMP_Q _R H | [7 empty] | R phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
220 |  |  |  |  | COMP_Q _R L | [7 empty] | R phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
221 |  |  |  |  | COMP_Q _S H | [7 empty] | S phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
222 |  |  |  |  | COMP_Q _S L | [7 empty] | S phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
223 |  |  |  |  | COMP_Q _T H | [7 empty] | T phase compensate reactive power for SVG(High) | [24 empty] | 0.1Var
224 |  |  |  |  | COMP_Q _T L | [7 empty] | T phase compensate reactive power for SVG(low) | [24 empty] | 0.1Var
225 |  |  |  |  | COMP HAR_I_R | [7 empty] | R phase compensate harmonic for SVG | [24 empty] | 0.1A
226 |  |  |  |  | COMP HAR_I_S | [7 empty] | S phase compensate harmonic for SVG | [24 empty] | 0.1A
227 |  |  |  |  | COMP HAR_I_T | [7 empty] | T phase compensate harmonic for SVG | [24 empty] | 0.1A
228 |  |  |  |  | bRS232AgingTe stOkFlag | [7 empty] | RS232AgingTestOkFlag | [18 empty] | 0-1
229 |  |  |  |  | bFanFaultBit | [7 empty] | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit Bit2: Fan 3 fault bit Bit3: Fan 4 fault bit Bit4-7: Reserved
230 |  |  |  |  | Sac H | [7 empty] | Output apparent power H | [24 empty] | 0.1W
231 |  |  |  |  | Sac L | [7 empty] | Output apparent power L | [24 empty] | 0.1W
232 |  |  |  |  | ReActPowerH | [7 empty] | Real Output Reactive Power H | [18 empty] | Int32 | [5 empty] | 0.1W
233 |  |  |  |  | ReActPowerL | [7 empty] | Real Output Reactive Power L
234 |  |  |  |  | ReActPowerMa xH | [7 empty] | Nominal Output Reactive Power H | [24 empty] | 0.1var
235 |  |  |  |  | ReActPowerMa xL | [7 empty] | Nominal Output Reactive Power L
236 |  |  |  |  | ReActPower_To talH | [7 empty] | Reactive power generation | [24 empty] | 0.1kwh
237 |  |  |  |  | ReActPower_To talL | [7 empty] | Reactive power generation
238 |  |  |  |  | bAfciStatus | [7 empty] | 0:Waiting 1:Self-check state 2:Detect pull arc state 3:Fault 4:Update
239 |  |  |  |  | uwPresentFFTVa lue [CHANNEL_A] | [7 empty] | PresentFFTValue [CHANNEL_A]
240 |  |  |  |  | uwPresentFFTVa lue [CHANNEL_B] | [7 empty] | PresentFFTValue [CHANNEL_B]
241 |  |  |  |  | DSP067 Debug Data1 | [7 empty] | DSP067 Debug Data1
242 |  |  |  |  | DSP067 Debug Data2 | [7 empty] | DSP067 Debug Data2
243 |  |  |  |  | DSP067 Debug Data3 | [7 empty] | DSP067 Debug Data3
244 |  |  |  |  | DSP067 Debug Data4 | [7 empty] | DSP067 Debug Data4
245 |  |  |  |  | DSP067 Debug Data5 | [7 empty] | DSP067 Debug Data5
246 |  |  |  |  | DSP067 Debug Data6 | [7 empty] | DSP067 Debug Data6
247 |  |  |  |  | DSP067 Debug Data7 | [7 empty] | DSP067 Debug Data7
248 |  |  |  |  | DSP067 Debug Data8 | [7 empty] | DSP067 Debug Data8
249 | [41 empty] | reserved
The eighth group for PV9-PV16 information
875 |  |  |  |  | Vpv9 | [7 empty] | PV9 voltage | [24 empty] | 0.1V
876 |  |  |  |  | PV9Curr | [7 empty] | PV9 Input current | [24 empty] | 0.1A
877 |  |  |  |  | Ppv9 H | [7 empty] | PV9 input power (High) | [24 empty] | 0.1W
878 |  |  |  |  | Ppv9 L | [7 empty] | PV9 input power (Low) | [24 empty] | 0.1W
879 |  |  |  |  | Vpv10 | [7 empty] | PV10 voltage | [24 empty] | 0.1V
880 |  |  |  |  | PV10Curr | [7 empty] | PV10 Input current | [24 empty] | 0.1A
881 |  |  |  |  | Ppv10 H | [7 empty] | PV10 input power (High) | [24 empty] | 0.1W
882 |  |  |  |  | Ppv10 L | [7 empty] | PV10 input power (Low) | [24 empty] | 0.1W
883 |  |  |  |  | Vpv11 | [7 empty] | PV11 voltage | [24 empty] | 0.1V
884 |  |  |  |  | PV11Curr | [7 empty] | PV11 Input current | [24 empty] | 0.1A
885 |  |  |  |  | Ppv11 H | [7 empty] | PV11 input power (High) | [24 empty] | 0.1W
886 |  |  |  |  | Ppv11 L | [7 empty] | PV11 input power (Low) | [24 empty] | 0.1W
887 |  |  |  |  | Vpv12 | [7 empty] | PV12 voltage | [24 empty] | 0.1V
888 |  |  |  |  | PV12Curr | [7 empty] | PV12 Input current | [24 empty] | 0.1A
889 |  |  |  |  | Ppv12 H | [7 empty] | PV12 input power (High) | [24 empty] | 0.1W
890 |  |  |  |  | Ppv12 L | [7 empty] | PV12 input power (Low) | [24 empty] | 0.1W
891 |  |  |  |  | Vpv13 | [7 empty] | PV13 voltage | [24 empty] | 0.1V
892 |  |  |  |  | PV13Curr | [7 empty] | PV13 Input current | [24 empty] | 0.1A
893 |  |  |  |  | Ppv13H | [7 empty] | PV13 input power (High) | [24 empty] | 0.1W
894 |  |  |  |  | Ppv13 L | [7 empty] | PV13 input power (Low) | [24 empty] | 0.1W
895 |  |  |  |  | Vpv14 | [7 empty] | PV14 voltage | [24 empty] | 0.1V
896 |  |  |  |  | PV14Curr | [7 empty] | PV14 Input current | [24 empty] | 0.1A
897 |  |  |  |  | Ppv14 H | [7 empty] | PV14 input power (High) | [24 empty] | 0.1W
898 |  |  |  |  | Ppv14 L | [7 empty] | PV14 input power (Low) | [24 empty] | 0.1W
899 |  |  |  |  | Vpv15 | [7 empty] | PV15 voltage | [24 empty] | 0.1V
900 |  |  |  |  | PV15Curr | [7 empty] | PV15 Input current | [24 empty] | 0.1A
901 |  |  |  |  | Ppv15 H | [7 empty] | PV15 input power (High) | [24 empty] | 0.1W
902 |  |  |  |  | Ppv15 L | [7 empty] | PV15 input power (Low) | [24 empty] | 0.1W
903 |  |  |  |  | Vpv16 | [7 empty] | PV16 voltage | [24 empty] | 0.1V
904 |  |  |  |  | PV16Curr | [7 empty] | PV16 Input current | [24 empty] | 0.1A
905 |  |  |  |  | Ppv16 H | [7 empty] | PV16 input power (High) | [24 empty] | 0.1W
906 |  |  |  |  | Ppv16 L | [7 empty] | PV16 input power (Low) | [24 empty] | 0.1W
907 |  |  |  |  | Epv9_today H | [7 empty] | PV9 energy today (High) | [24 empty] | 0.1kWh
908 |  |  |  |  | Epv9_today L | [7 empty] | PV9 energy today (Low) | [24 empty] | 0.1kWh
909 |  |  |  |  | Epv9_total H | [7 empty] | PV9 energy total (High) | [24 empty] | 0.1kWh
910 |  |  |  |  | Epv9_total L | [7 empty] | PV9 energy total (Low) | [24 empty] | 0.1kWh
911 |  |  |  |  | Epv10_today H | [7 empty] | PV10 energy today (High) | [24 empty] | 0.1kWh
912 |  |  |  |  | Epv10_today L | [7 empty] | PV10 energy today (Low) | [24 empty] | 0.1kWh
913 |  |  |  |  | Epv10_total H | [7 empty] | PV10 energy total (High) | [24 empty] | 0.1kWh
914 |  |  |  |  | Epv10_total L | [7 empty] | PV10 energy total (Low) | [24 empty] | 0.1kWh
915 |  |  |  |  | Epv11_today H | [7 empty] | PV11 energy today (High) | [24 empty] | 0.1kWh
916 |  |  |  |  | Epv11_today L | [7 empty] | PV11 energy today (Low) | [24 empty] | 0.1kWh
917 |  |  |  |  | Epv11_total H | [7 empty] | PV11 energy total (High) | [24 empty] | 0.1kWh
918 |  |  |  |  | Epv11_total L | [7 empty] | PV11 energy total (Low) | [24 empty] | 0.1kWh
919 |  |  |  |  | Epv12_today H | [7 empty] | PV12 energy today (High) | [24 empty] | 0.1kWh
920 |  |  |  |  | Epv12_today L | [7 empty] | PV12 energy today (Low) | [24 empty] | 0.1kWh
921 |  |  |  |  | Epv12_total H | [7 empty] | PV12 energy total (High) | [24 empty] | 0.1kWh
922 |  |  |  |  | Epv12_total L | [7 empty] | PV12 energy total (Low) | [24 empty] | 0.1kWh
923 |  |  |  |  | Epv13_today H | [7 empty] | PV13 energy today (High) | [24 empty] | 0.1kWh
924 |  |  |  |  | Epv13_today L | [7 empty] | PV13 energy today (Low) | [24 empty] | 0.1kWh
925 |  |  |  |  | Epv13_total H | [7 empty] | PV13 energy total (High) | [24 empty] | 0.1kWh
926 |  |  |  |  | Epv13_total L | [7 empty] | PV13 energy total (Low) | [24 empty] | 0.1kWh
927 |  |  |  |  | Epv14_today H | [7 empty] | PV14 energy today (High) | [24 empty] | 0.1kWh
928 |  |  |  |  | Epv14_today L | [7 empty] | PV14 energy today (Low) | [24 empty] | 0.1kWh
929 |  |  |  |  | Epv14_total H | [7 empty] | PV14 energy total (High) | [24 empty] | 0.1kWh
930 |  |  |  |  | Epv14_total L | [7 empty] | PV14 energy total (Low) | [24 empty] | 0.1kWh
931 |  |  |  |  | Epv15_today H | [7 empty] | PV15 energy today (High) | [24 empty] | 0.1kWh
932 |  |  |  |  | Epv15_today L | [7 empty] | PV15 energy today (Low) | [24 empty] | 0.1kWh
933 |  |  |  |  | Epv15_total H | [7 empty] | PV15 energy total (High) | [24 empty] | 0.1kWh
934 |  |  |  |  | Epv15_total L | [7 empty] | PV15 energy total (Low) | [24 empty] | 0.1kWh
935 |  |  |  |  | Epv16_today H | [7 empty] | PV16 energy today (High) | [24 empty] | 0.1kWh
936 |  |  |  |  | Epv16_today L | [7 empty] | PV16 energy today (Low) | [24 empty] | 0.1kWh
937 |  |  |  |  | Epv16_total H | [7 empty] | PV16 energy total (High) | [24 empty] | 0.1kWh
938 |  |  |  |  | Epv16_total L | [7 empty] | PV16 energy total (Low) | [24 empty] | 0.1kWh
939 |  |  |  |  | PID PV9+ Voltage | [7 empty] | PID PV9PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
940 |  |  |  |  | PID PV9+ Current | [7 empty] | PID PV9PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
941 |  |  |  |  | PID PV10+ Voltage | [7 empty] | PID PV10PE/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
942 |  |  |  |  | PID PV10+ Current | [7 empty] | PID PV10PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
943 |  |  |  |  | PID PV11+ Voltage | [7 empty] | PID PV11PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
944 |  |  |  |  | PID PV11+ Current | [7 empty] | PID PV11PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
945 |  |  |  |  | PID PV12+ Voltage | [7 empty] | PID PV12PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
946 |  |  |  |  | PID PV12+ Current | [7 empty] | PID PV12PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
947 |  |  |  |  | PID PV13+ Voltage | [7 empty] | PID PV13PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
948 |  |  |  |  | PID PV13+ Current | [7 empty] | PID PV13PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
949 |  |  |  |  | PID PV14+ Voltage | [7 empty] | PID PV14PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
950 |  |  |  |  | PID PV14+ Current | [7 empty] | PID PV14PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
951 |  |  |  |  | PID PV15+ Voltage | [7 empty] | PID PV15PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
952 |  |  |  |  | PID PV15+ Current | [7 empty] | PID PV15PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
953 |  |  |  |  | PID PV16+ Voltage | [7 empty] | PID PV16PE Volt/ Flyspan voltage (MAX HV) | [18 empty] | 0~1000V | [5 empty] | 0.1V
954 |  |  |  |  | PID PV16+ Current | [7 empty] | PID PV16PE Current | [18 empty] | -10~10m A | [5 empty] | 0.1mA
955 |  |  |  |  | V _String17 | [7 empty] | PV String 17 voltage | [24 empty] | 0.1V
956 |  |  |  |  | Curr _String17 | [7 empty] | PV String 17 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
957 |  |  |  |  | V _String18 | [7 empty] | PV String 18 voltage | [24 empty] | 0.1V
958 |  |  |  |  | Curr _String18 | [7 empty] | PV String 18 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
959 |  |  |  |  | V _String19 | [7 empty] | PV String 19 voltage | [24 empty] | 0.1V
960 |  |  |  |  | Curr _String19 | [7 empty] | PV String 19 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
961 |  |  |  |  | V _String20 | [7 empty] | PV String 20 voltage | [24 empty] | 0.1V
962 |  |  |  |  | Curr _String20 | [7 empty] | PV String 20 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
963 |  |  |  |  | V _String21 | [7 empty] | PV String 21 voltage | [24 empty] | 0.1V
964 |  |  |  |  | Curr _String21 | [7 empty] | PV String 21 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
965 |  |  |  |  | V _String22 | [7 empty] | PV String22 voltage | [24 empty] | 0.1V
966 |  |  |  |  | Curr _String22 | [7 empty] | PV String 22 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
967 |  |  |  |  | V _String23 | [7 empty] | PV String 23 voltage | [24 empty] | 0.1V
968 |  |  |  |  | Curr _String23 | [7 empty] | PV String 23 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
969 |  |  |  |  | V _String24 | [7 empty] | PV String 24 voltage | [24 empty] | 0.1V
970 |  |  |  |  | Curr _String24 | [7 empty] | PV String 24 Current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
971 |  |  |  |  | V _String25 | [7 empty] | PV String 25 voltage | [24 empty] | 0.1V
972 |  |  |  |  | Curr _String25 | [7 empty] | PV String 25 Current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
973 |  |  |  |  | V _String26 | [7 empty] | PV String 26 voltage | [24 empty] | 0.1V
974 |  |  |  |  | Curr _String26 | [7 empty] | PV String 26 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
975 |  |  |  |  | V _String27 | [7 empty] | PV String 27 voltage | [24 empty] | 0.1V
976 |  |  |  |  | Curr _String27 | [7 empty] | PV String 27 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
977 |  |  |  |  | V _String28 | [7 empty] | PV String 28 voltage | [24 empty] | 0.1V
978 |  |  |  |  | Curr _String28 | [7 empty] | PV String 28 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
979 |  |  |  |  | V _String29 | [7 empty] | PV String 29 voltage | [24 empty] | 0.1V
980 |  |  |  |  | Curr _String29 | [7 empty] | PV String 29 Current | [18 empty] | -15A~15 A | [5 empty] | 0.1A
981 |  |  |  |  | V _String30 | [7 empty] | PV String 30 voltage | [24 empty] | 0.1V
982 |  |  |  |  | Curr _String30 | [7 empty] | PV String 30 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
983 |  |  |  |  | V _String31 | [7 empty] | PV String 31 voltage | [24 empty] | 0.1V
984 |  |  |  |  | Curr _String31 | [7 empty] | PV String 31 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
985 |  |  |  |  | V _String32 | [7 empty] | PV String 32 voltage | [24 empty] | 0.1V
986 |  |  |  |  | Curr _String32 | [7 empty] | PV String 32 Current | [18 empty] | -15~15A | [5 empty] | 0.1A
987 |  |  |  |  | StrUnmatch2 | [7 empty] | Bit0~15: String 17~32 unmatch
988 |  |  |  |  | StrCurrentUnbl ance2 | [7 empty] | Bit0~15:String 17~32 current unblance
989 |  |  |  |  | StrDisconnect2 | [7 empty] | Bit0~15: String 17~32 disconnect
990 |  |  |  |  | PV Warning Value | [7 empty] | PV Warning Value (PV9-PV16) Contains PV9~16 abnormal,Boost9~16 Drive anomalies
991 |  |  |  |  | StrWaringvalue 1 | [7 empty] | string1~string16 abnormal
992 |  |  |  |  | StrWaringvalue 2 | [7 empty] | string17~string32 abnormal
… | [41 empty] | Reserve
999 |  |  |  |  | SystemCmd | [7 empty] | M3 to DSP system command | [28 empty] | system command
Ninth group for Storage power
1000 |  |  |  |  | uwSysWorkMo de | [7 empty] | System work mode 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03:SysFault module 0x04: Flash module 0x05:PVBATOnlinemodu le, 0x06:BatOnline module, 0x07:PVOfflineMode module, 0x08:BatOfflineMode module, | [28 empty] | The working mode displayed by the monitoring to the customer is: 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash module 0x05¦0x06¦0 x07¦0x08¦0x 09:normal module
1001 |  |  |  |  | Systemfault word0 | [7 empty] | System fault word0 | [28 empty] | Please refer to the fault descri-ption of Hybrid
1002 |  |  |  |  | Systemfault word1 | [7 empty] | System fault word1
1003 |  |  |  |  | Systemfault word2 | [7 empty] | System fault word2
1004 |  |  |  |  | Systemfault word3 | [7 empty] | System fault word3
1005 |  |  |  |  | Systemfault word4 | [7 empty] | System fault word4
1006 |  |  |  |  | Systemfault word5 | [7 empty] | System fault word5
1007 |  |  |  |  | Systemfault word6 | [7 empty] | System fault word6
1008 |  |  |  |  | Systemfault word7 | [7 empty] | System fault word7
1009 |  |  |  |  | Pdischarge1 H | [7 empty] | Discharge power(high) | [24 empty] | 0.1W
1010 |  |  |  |  | Pdischarge1 L | [7 empty] | Discharge power (low) | [24 empty] | 0.1W
1011 |  |  |  |  | Pcharge1 H | [7 empty] | Charge power(high) | [24 empty] | 0.1W
1012 |  |  |  |  | Pcharge1 L | [7 empty] | Charge power (low) | [24 empty] | 0.1W
1013 |  |  |  |  | Vbat | [7 empty] | Battery voltage | [24 empty] | 0.1V
1014 |  |  |  |  | SOC | [7 empty] | State of charge Capacity | [13 empty] | 0-100 | [10 empty] | 1% |  |  |  | lith/leadacid
1015 |  |  |  |  | Pactouser H |  |  |  |  | R |  |  | AC power to user H | [24 empty] | 0.1w
1016 |  |  |  |  | Pactouser L |  |  |  |  | R |  |  | AC power to user L | [24 empty] | 0.1w
1017 |  |  |  |  | Pactouser H |  |  |  |  | S |  |  | Pactouser S | [7 empty] | H | [16 empty] | 0.1w
1018 |  |  |  |  | Pactouser L |  |  |  |  | S |  |  | Pactouser S | [7 empty] | L | [16 empty] | 0.1w
1019 |  |  |  |  | Pactouser H |  |  |  |  | T |  |  | Pactouser T | [7 empty] | H | [16 empty] | 0.1w
1020 |  |  |  |  | Pactouser L |  |  |  |  | T |  |  | Pactouser T | [7 empty] | H | [16 empty] | 0.1w
1021 |  |  |  |  | PactouserTotal H | [7 empty] | AC power to user total H | [24 empty] | 0.1w
1022 |  |  |  |  | PactouserTotal L | [7 empty] | AC power to user total L | [24 empty] | 0.1w
1023 |  |  |  |  | Pac to grid R H | [7 empty] | AC power to grid H | [24 empty] | 0.1w |  |  |  | Ac output
1024 |  |  |  |  | Pac to grid R |  |  |  |  | L |  |  | AC power to grid L | [24 empty] | 0.1w
1025 |  |  |  |  | Pactogrid S |  |  |  |  | H | [27 empty] | 0.1w
1026 |  |  |  |  | Pactogrid S |  |  |  |  | L | [27 empty] | 0.1w
1027 |  |  |  |  | Pactogrid T H | [32 empty] | 0.1w
1028 |  |  |  |  | Pactogrid T L | [32 empty] | 0.1w
1029 |  |  |  |  | Pactogrid total H | [7 empty] | AC power to grid total H | [24 empty] | 0.1w
1030 |  |  |  |  | Pactogrid total L | [7 empty] | AC power to grid total L | [24 empty] | 0.1w
1031 |  |  |  |  | PLocalLoad H |  |  |  |  | R |  |  | INV power to local load H | [24 empty] | 0.1w
1032 |  |  |  |  | PLocalLoad L |  |  |  |  | R |  |  | INV power to local load L | [24 empty] | 0.1w
1033 |  |  |  |  | PLocalLoad H |  |  |  |  | S | [27 empty] | 0.1w
1034 |  |  |  |  | PLocalLoad L |  |  |  |  | S | [27 empty] | 0.1w
1035 |  |  |  |  | PLocalLoadT H | [32 empty] | 0.1w
1036 |  |  |  |  | PLocalLoadT |  |  |  |  | L | [27 empty] | 0.1w
1037 |  |  |  |  | PLocalLoad total H | [7 empty] | INV power to local load total H | [24 empty] | 0.1w
1038 |  |  |  |  | PLocalLoad total L | [7 empty] | INV power to local load total L | [24 empty] | 0.1w
1039 |  |  |  |  | IPM Temperature | [7 empty] | REC Temperature | [24 empty] | 0.1℃ |  |  |  | No use
1040 |  |  |  |  | Battery Temperature | [7 empty] | Battery Temperature | [24 empty] | 0.1℃ |  |  |  | Lead acid/lithium battery temp
1041 |  |  |  |  | SP DSP Status | [7 empty] | SP state | [28 empty] | CHG/DisCH G
1042 |  |  |  |  | SP Bus Volt | [7 empty] | SP BUS2 Volt | [24 empty] | 0.1V
1043
Power generation data
1044 |  |  |  |  | Etouser_today H | [7 empty] | Energy high |  |  |  |  | to |  | user |  |  |  | today | [13 empty] | 0.1kwh
1045 |  |  |  |  | Etouser_today L | [7 empty] | Energy low |  |  |  |  | to |  | user |  |  |  | today | [13 empty] | 0.1kwh
1046 |  |  |  |  | Etouser_total H | [7 empty] | Energy to user total high | [24 empty] | 0.1kwh
1047 |  |  |  |  | Etouser_ total L | [7 empty] | Energy to user total high | [24 empty] | 0.1kwh
1048 |  |  |  |  | Etogrid_today H | [7 empty] | Energy high |  |  |  |  | to |  | grid |  |  |  | today | [13 empty] | 0.1kwh
1049 |  |  |  |  | Etogrid _today L | [7 empty] | Energy to grid today low | [24 empty] | 0.1kwh
1050 |  |  |  |  | Etogrid _total H | [7 empty] | Energy to grid total high | [24 empty] | 0.1kwh
1051 |  |  |  |  | Etogrid _ total L | [7 empty] | Energy to grid total high | [24 empty] | 0.1kwh
1052 |  |  |  |  | Edischarge1_to day H | [7 empty] | Discharge energy1 today | [24 empty] | 0.1kwh
1053 |  |  |  |  | Edischarge1_to day L | [7 empty] | Discharge energy1 today | [24 empty] | 0.1kwh
1054 |  |  |  |  | Edischarge1_to tal H | [7 empty] | Total discharge energy1 (high) | [24 empty] | 0.1kwh
1055 |  |  |  |  | Edischarge1_to tal L | [7 empty] | Total discharge energy1 (low) | [24 empty] | 0.1kwh
1056 |  |  |  |  | Echarge1_toda y H | [7 empty] | Charge1 energy today | [24 empty] | 0.1kwh
1057 |  |  |  |  | Echarge1_toda y L | [7 empty] | Charge1 energy today | [24 empty] | 0.1kwh
1058 |  |  |  |  | Echarge1_total H | [7 empty] | Charge1 energy total | [24 empty] | 0.1kwh
1059 |  |  |  |  | Echarge1_total L | [7 empty] | Charge1 energy total | [24 empty] | 0.1kwh
1060 |  |  |  |  | ELocalLoad_Tod ay H | [7 empty] | Local load energy today | [24 empty] | 0.1kwh
1061 |  |  |  |  | ELocalLoad_Tod ay L | [7 empty] | Local load energy today | [24 empty] | 0.1kwh
1062 |  |  |  |  | ELocalLoad_Tot al H | [7 empty] | Local load energy total | [24 empty] | 0.1kwh
1063 |  |  |  |  | ELocalLoad_Tot al L | [7 empty] | Local load energy total | [24 empty] | 0.1kwh
1064 |  |  |  |  | dwExportLimit ApparentPower | [7 empty] | Export Limit Apparent Power H | [24 empty] | 0.1kwh
1065 |  |  |  |  | dwExportLimit ApparentPower | [7 empty] | Export Limit Apparent Power L | [24 empty] | 0.1kwh
1066 |  |  |  |  | reserved | [36 empty] | reserved
Ups information (offline)
1067 |  |  |  |  | EPS Fac | [7 empty] | UPSfrequency | [13 empty] | 5000/6000 | [10 empty] | 0.01Hz
1068 |  |  |  |  | EPS Vac1 | [7 empty] | UPS phase R output voltage | [13 empty] | 2300 | [10 empty] | 0.1V
1069 |  |  |  |  | EPS Iac1 | [7 empty] | UPS phase R output current | [24 empty] | 0.1A
1070 |  |  |  |  | EPS Pac1 H | [7 empty] | UPS phase R output power (H) | [24 empty] | 0.1VA
1071 |  |  |  |  | EPS Pac1 L | [7 empty] | UPS phase R output power (L) | [24 empty] | 0.1VA
1072 |  |  |  |  | EPS Vac2 | [7 empty] | UPS phase S output voltage | [24 empty] | 0.1V
1073 |  |  |  |  | EPS Iac2 | [7 empty] | UPS phase S output current | [24 empty] | 0.1A |  |  |  | Not used
1074 |  |  |  |  | EPS Pac2 H | [7 empty] | UPS phase S output power (H) | [24 empty] | 0.1VA
1075 |  |  |  |  | EPS Pac2 L | [7 empty] | UPS phase S output power (L) | [24 empty] | 0.1VA
1076 |  |  |  |  | EPS Vac3 | [7 empty] | UPS phase T output voltage | [24 empty] | 0.1V
1077 |  |  |  |  | EPS Iac3 | [7 empty] | UPS phase T output current | [24 empty] | 0.1A |  |  |  | Not used
1078 |  |  |  |  | EPS Pac3 H | [7 empty] | UPS phase T output power (H) | [24 empty] | 0.1VA
1079 |  |  |  |  | EPS Pac3 L | [7 empty] | UPS phase T output power (L) | [24 empty] | 0.1VA
1080 |  |  |  |  | loadpercent | [7 empty] | Load percent of UPS ouput | [13 empty] | 0-100 | [10 empty] | 1%
1081 |  |  |  |  | PF | [7 empty] | Power factor | [13 empty] | 0-2 | [10 empty] | 0.1 |  |  |  | Primary Value+1
BMS Infomation
1082 |  |  |  |  | BMS_StatusOld | [7 empty] | StatusOld from BMS | [13 empty] | Detail information, refer to document : GrowattxxSxxP ESS Protocol;
1083 |  |  |  |  | BMS_Status | [7 empty] | Status from BMS | [28 empty] | W/R
1084 |  |  |  |  | BMS_Error Old | [7 empty] | Error info Old from BMS
1085 |  |  |  |  | BMS_Error | [7 empty] | Errorinfomation from BMS
1086 |  |  |  |  | BMS_SOC | [7 empty] | SOC from BMS | [28 empty] | R SPH6K
1087 |  |  |  |  | BMS_BatteryVo lt | [7 empty] | Battery voltage from BMS | [28 empty] | R SPH6K
1088 |  |  |  |  | BMS_BatteryCu rr | [7 empty] | Battery current from BMS
1089 |  |  |  |  | BMS_BatteryTe mp | [7 empty] | Battery temperature from BMS
1090 |  |  |  |  | BMS_MaxCurr | [7 empty] | Max charge/discharge current from BMS (pylon)
1091 |  |  |  |  | BMS_GaugeRM | [7 empty] | Gauge RM from BMS
1092 |  |  |  |  | BMS_GaugeFCC | [7 empty] | Gauge FCC from BMS
1093 |  |  |  |  | BMS_FW
1094 |  |  |  |  | BMS_DeltaVolt | [7 empty] | Delta V from BMS
1095 |  |  |  |  | BMS_CycleCnt | [7 empty] | Cycle Count from BMS
1096 |  |  |  |  | BMS_SOH | [7 empty] | SOH from BMS
1097 |  |  |  |  | BMS_Constant Volt | [7 empty] | CV voltage from BMS
1098 |  |  |  |  | BMS_WarnInfo Old | [7 empty] | Warning info old from BMS
1099 |  |  |  |  | BMS_WarnInfo | [7 empty] | Warning info from BMS
1100 |  |  |  |  | BMS_GaugeICC urr | [7 empty] | Gauge IC current from BMS
1101 |  |  |  |  | BMS_MCUVersi on | [7 empty] | MCU Software version from BMS
1102 |  |  |  |  | BMS_GaugeVer sion | [7 empty] | Gauge Version from BMS
1103 |  |  |  |  | BMS_wGaugeF RVersion_ L | [7 empty] | Gauge FR Version L16 from BMS
1104 |  |  |  |  | BMS_wGaugeF RVersion_H | [7 empty] | Gauge FR Version H16 from BMS
1105 |  |  |  |  | BMS_BMSInfo | [7 empty] | BMSInformation from BMS
1106 |  |  |  |  | BMS_PackInfo | [7 empty] | Pack Information from BMS
1107 |  |  |  |  | BMS_UsingCap | [7 empty] | Using Cap from BMS
1108 |  |  |  |  | uwMaxCellVolt | [7 empty] | Maximum single battery voltage | [24 empty] | 0.001V
1109 |  |  |  |  | uwMinCellVolt | [7 empty] | Lowest single battery voltage | [24 empty] | 0.001V
1110 |  |  |  |  | bModuleNum | [7 empty] | Battery parallel number | [24 empty] | 1
1111 |  |  |  |  | bBatNum | [7 empty] | Number of batteries | [24 empty] | 1
1112 |  |  |  |  | uwMaxVoltCell No | [7 empty] | Max Voltage Cell No | [24 empty] | 1
1113 |  |  |  |  | uwMinVoltCell No | [7 empty] | Min Voltage Cell No | [24 empty] | 1
1114 |  |  |  |  | uwMaxTemprC ell_10T | [7 empty] | Max Tempr Cell_10T | [24 empty] | 0.1℃
1115 |  |  |  |  | uwMinTemprCe ll_10T | [7 empty] | Min Tempr Cell_10T | [24 empty] | 0.1℃
1116 |  |  |  |  | uwMaxTemprC ellNo | [7 empty] | Max Volt Tempr Cell No | [24 empty] | 1
1117 |  |  |  |  | uwMinTemprCe llNo | [7 empty] | Min Volt Tempr Cell No | [24 empty] | 1
1118 |  |  |  |  | Protect pack ID | [7 empty] | Faulty Battery Address | [24 empty] | 1
1119 |  |  |  |  | MaxSOC | [7 empty] | Parallel maximum SOC | [24 empty] | 1%
1120 |  |  |  |  | MinSOC | [7 empty] | Parallel minimum SOC | [24 empty] | 1%
1121 |  |  |  |  | BMS_Error2 | [7 empty] | Battery Protection 2 | [24 empty] | - |  |  |  | CAN ID:0x323 Byte4~5
1122 |  |  |  |  | BMS_Error3 | [7 empty] | Battery Protection3 | [24 empty] | - |  |  |  | CAN ID:0x323 Byte6
1123 |  |  |  |  | BMS_WarnInfo 2 | [7 empty] | Battery Warn2 | [24 empty] | - |  |  |  | CAN ID:0x323 Byte7
1124 |  |  |  |  | AC Charge Energy Today H | [7 empty] | AC Charge Energy today | [24 empty] | kwh |  |  |  | Energy today
Ninth group reserved for storage power
1125 |  |  |  |  | ACCharge Energy TodayL | [7 empty] | AC Charge Energy today | [24 empty] | kwh
1126 |  |  |  |  | AC Charge Energy Total H | [36 empty] | Energy total
1127 |  |  |  |  | ACCharge Energy Total L
1128 |  |  |  |  | AC Charge Power H | [7 empty] | AC Charge Power | [24 empty] | W
1129 |  |  |  |  | AC Charge Power L | [7 empty] | AC Charge Power | [24 empty] | w
1130 |  |  |  |  | 70% INV Power adjust | [7 empty] | uwGridPower_70_AdjEE _SP | [24 empty] | W
1131 |  |  |  |  | ExtraACPower to grid_H | [7 empty] | Extra inverte AC Power to grid High, For SPA connect inverter | [28 empty] | SPA used
1132 |  |  |  |  | ExtraACPower to grid_L | [7 empty] | Extrainverte AC Power to grid Low | [28 empty] | SPA used
1133 |  |  |  |  | Eextra_today H | [7 empty] | Extra inverter PowerTOUser_Extra today (high) | [13 empty] | R | [10 empty] | 0.1kWh |  |  |  | SPA used
1134 |  |  |  |  | Eextra_today L | [7 empty] | Extra inverter PowerTOUser_Extra today (low) | [13 empty] | R | [10 empty] | 0.1kWh |  |  |  | SPA used
1135 |  |  |  |  | Eextra_total H | [7 empty] | Extra inverter PowerTOUser_Extra total(high) | [24 empty] | 0.1kWh |  |  |  | SPA used
1136 |  |  |  |  | Eextra_total L | [7 empty] | Extra inverter PowerTOUser_Extra total(low) | [24 empty] | 0.1kWh |  |  |  | SPA used
1137 |  |  |  |  | Esystem_today H | [7 empty] | System electric energy today H | [24 empty] | 0.1kWh |  |  |  | SPA used System electric energy today H
1138 |  |  |  |  | Esystem_ today L | [7 empty] | System electric energy today L | [24 empty] | 0.1kWh |  |  |  | SPA used System electric energy today L
1139 |  |  |  |  | Esystem_total H | [7 empty] | System electric energy total H | [24 empty] | 0.1kWh |  |  |  | SPA used System electric energy total H
1140 |  |  |  |  | Esystem_ total L | [7 empty] | System electric energy total L | [24 empty] | 0.1kWh |  |  |  | SPA used System electric energy total L
1141 |  |  |  |  | Eself_today H | [7 empty] | self electric energy today H | [24 empty] | 0.1kWh |  |  |  | self electric energy today H
1142 |  |  |  |  | Eself_ today L | [7 empty] | self electric energy today L | [24 empty] | 0.1kWh |  |  |  | self electric energy today L
1143 |  |  |  |  | Eself_total H | [7 empty] | self electric energy total H | [24 empty] | 0.1kWh |  |  |  | self electric energy total H
1144 |  |  |  |  | Eself_ total L | [7 empty] | self electric energy total L | [24 empty] | 0.1kWh |  |  |  | self electric energy total L
1145 |  |  |  |  | PSystem H | [7 empty] | System power H | [24 empty] | 0.1w |  |  |  | System power H
1146 |  |  |  |  | PSystem L | [7 empty] | System power L | [24 empty] | 0.1w |  |  |  | System power L
1147 |  |  |  |  | PSelf H | [7 empty] | self power H | [24 empty] | 0.1w |  |  |  | self power H
1148 |  |  |  |  | PSelf L | [7 empty] | self power L | [24 empty] | 0.1w |  |  |  | self power L
1149 |  |  |  |  | EPVAll_Today H | [7 empty] | PV electric energy today H | [24 empty] | 0.1kWh
1150 |  |  |  |  | EPVAll_Today L | [7 empty] | PV electric energy today L | [24 empty] | 0.1kWh
1151 |  |  |  |  | AcDischarge PackSn | [7 empty] | Discharge power pack serial number | [13 empty] | R
1152 |  |  |  |  | Acdischarge power_H | [7 empty] | Cumulative discharge power high 16-bit byte | [13 empty] | R | [10 empty] | 0.1kwh
1153 |  |  |  |  | Acdischarge power_L | [7 empty] | Cumulative discharge power low 16-bit byte | [13 empty] | R | [10 empty] | 0.1kwh
1154 |  |  |  |  | AcCharge PackSn | [7 empty] | charge power pack serial number | [13 empty] | R
1155 |  |  |  |  | AcCharge power_H | [7 empty] | Cumulative charge power high 16-bit byte | [13 empty] | R | [10 empty] | 0.1kwh
1156 |  |  |  |  | AcCharge power_L | [7 empty] | Cumulative charge power low 16-bit byte | [13 empty] | R | [10 empty] | 0.1kwh
1157 |  |  |  |  | First Batt Fault Sn | [7 empty] | First Battery Fault Sn | [13 empty] | R
1158 |  |  |  |  | Second Batt Fault Sn | [7 empty] | Second Batt Fault Sn | [13 empty] | R
1159 |  |  |  |  | Third Batt Fault Sn | [7 empty] | Third Batt Fault Sn | [13 empty] | R
1160 |  |  |  |  | Fourth Batt Fault Sn | [7 empty] | Fourth Batt Fault Sn | [13 empty] | R
1161 |  |  |  |  | Battery history fault code 1 | [7 empty] | Battery history fault code 1 | [13 empty] | R
1162 |  |  |  |  | Battery history fault code 2 | [7 empty] | Battery history fault code 2 | [13 empty] | R
1163 |  |  |  |  | Battery history fault code 3 | [7 empty] | Battery history fault code 3 | [13 empty] | R
1164 |  |  |  |  | Battery history fault code 4 | [7 empty] | Battery history fault code 4 | [13 empty] | R
1165 |  |  |  |  | Battery history fault code 5 | [7 empty] | Battery history fault code 5 | [13 empty] | R
1166 |  |  |  |  | Battery history fault code 6 | [7 empty] | Battery history fault code 6 | [13 empty] | R
1167 |  |  |  |  | Battery history fault code 7 | [7 empty] | Battery history fault code 7 | [13 empty] | R
1168 |  |  |  |  | Battery history fault code 8 | [7 empty] | Battery history fault code 8 | [13 empty] | R
1169 |  |  |  |  | Number of battery codes | [7 empty] | Number of battery codes PACK number + BIC forward and reverse codes | [13 empty] | R
1170 |  |  |  |  | reversed | [36 empty] | reversed
…… |  |  |  |  | reversed | [36 empty] | reversed
1199 |  |  |  |  | NewEPowerCal cFlag | [7 empty] | Intelligent reading is used to identify software compatibility features | [28 empty] | 0:Old energy calculation; 1:new energy calculation
1200 |  |  |  |  | MaxCellVolt | [7 empty] | Maximum cell voltage | [13 empty] | R | [10 empty] | 0.001V
1201 |  |  |  |  | MinCellVolt | [7 empty] | Minimum cell voltage | [13 empty] | R | [10 empty] | 0.001V
1202 |  |  |  |  | ModuleNum | [7 empty] | Number of Battery modules | [13 empty] | R
1203 |  |  |  |  | TotalCellNum | [7 empty] | Total number of cells | [13 empty] | R
1204 |  |  |  |  | MaxVoltCellNo | [7 empty] | MaxVoltCellNo | [13 empty] | R
1205 |  |  |  |  | MinVoltCellNo | [7 empty] | MinVoltCellNo | [13 empty] | R
1206 |  |  |  |  | MaxTemprCell_ 10T | [7 empty] | MaxTemprCell_10T | [13 empty] | R | [10 empty] | 0.1℃
1207 |  |  |  |  | MinTemprCell_ 10T | [7 empty] | MinTemprCell_10T | [13 empty] | R | [10 empty] | 0.1℃
1208 |  |  |  |  | MaxTemprCellN o | [7 empty] | MaxTemprCellNo | [13 empty] | R
1209 |  |  |  |  | MinTemprCellN o | [7 empty] | MinTemprCellNo | [13 empty] | R
1210 |  |  |  |  | ProtectPackID | [7 empty] | Fault Pack ID | [13 empty] | R
1211 |  |  |  |  | MaxSOC | [7 empty] | Parallel maximum SOC | [13 empty] | R | [10 empty] | 1%
1212 |  |  |  |  | MinSOC | [7 empty] | Parallel minimum SOC | [13 empty] | R | [10 empty] | 1%
1213 |  |  |  |  | BatProtect1Add | [7 empty] | BatProtect1Add | [13 empty] | R
1214 |  |  |  |  | BatProtect2Add | [7 empty] | BatProtect2Add | [13 empty] | R
1215 |  |  |  |  | BatWarn1Add | [7 empty] | BatWarn1Add | [13 empty] | R
1216 |  |  |  |  | BMS_HighestSo ftVersion | [7 empty] | BMS_HighestSoftVersio n | [13 empty] | R
1217 |  |  |  |  | BMS_Hardware Version | [7 empty] | BMS_HardwareVersion | [13 empty] | R
1218 |  |  |  |  | BMS_RequestT ype | [7 empty] | BMS_RequestType | [13 empty] | R
…… |  |  |  |  | reversed | [36 empty] | reversed
1248 |  |  |  |  | bKeyAgingTest OkFlag | [7 empty] | Success sign of key detection before aging | [28 empty] | 1:Finished test 0:test not completed
1249 | [41 empty] | reversed
thirteen group for Storage power’s SPA
2000 |  |  |  |  | Inverter Status | [10 empty] | Inverter run state | [25 empty] | SPA: 0:waiting 1:normal 3:fault
…… |  |  |  |  | reversed
2035 |  |  |  |  | Pac H | [10 empty] | Output power (high) | [21 empty] | 0.1W |  |  |  | SPA
2036 |  |  |  |  | Pac L | [10 empty] | Output power (low) | [21 empty] | 0.1W |  |  |  | SPA
2037 |  |  |  |  | Fac | [10 empty] | Grid frequency | [21 empty] | 0.01Hz |  |  |  | SPA
2038 |  |  |  |  | Vac1 | [10 empty] | Three/single phase grid voltage | [21 empty] | 0.1V |  |  |  | SPA
2039 |  |  |  |  | Iac1 | [10 empty] | Three/single phase grid output current | [21 empty] | 0.1A |  |  |  | SPA
2040 |  |  |  |  | Pac1 H | [10 empty] | Three/single phase grid output watt VA (high) | [21 empty] | 0.1VA |  |  |  | SPA
2041 |  |  |  |  | Pac1 L | [10 empty] | Three/single phase grid output watt VA(low) | [21 empty] | 0.1VA |  |  |  | SPA
…… |  |  |  |  | reversed
2053 |  |  |  |  | Eac today H | [10 empty] | Today generate energy (high) | [21 empty] | 0.1kWh |  |  |  | SPA
2054 |  |  |  |  | Eac today L | [10 empty] | Today generate energy (low) | [21 empty] | 0.1kWh |  |  |  | SPA
2055 |  |  |  |  | Eac total H | [10 empty] | Total generate energy (high) | [21 empty] | 0.1kWh |  |  |  | SPA
2056 |  |  |  |  | Eac total L | [10 empty] | Total generate energy (low) | [21 empty] | 0.1kWh |  |  |  | SPA
2057 |  |  |  |  | Time total H | [10 empty] | Work time total (high) | [21 empty] | 0.5s |  |  |  | SPA
2058 |  |  |  |  | Time total L | [10 empty] | Work time total (low) | [21 empty] | 0.5s |  |  |  | SPA
… |  |  |  |  | reversed
2093 |  |  |  |  | Temp1 | [10 empty] | Inverter temperature | [21 empty] | 0.1C |  |  |  | SPA
2094 |  |  |  |  | Temp2 | [10 empty] | The inside IPM in inverter Temperature | [21 empty] | 0.1C |  |  |  | SPA
2095 |  |  |  |  | Temp3 | [10 empty] | Boost temperature | [21 empty] | 0.1C |  |  |  | SPA
2096 |  |  |  |  | Temp4 | [36 empty] | reserved
2097 |  |  |  |  | uwBatVolt_DSP | [10 empty] | BatVolt_DSP | [21 empty] | 0.1V |  |  |  | BatVolt(DSP )
2098 |  |  |  |  | P Bus Voltage | [10 empty] | P Bus inside Voltage | [21 empty] | 0.1V |  |  |  | SPA
2099 |  |  |  |  | N Bus Voltage | [10 empty] | N Bus inside Voltage | [21 empty] | 0.1V |  |  |  | SPA
2100 |  |  |  |  | RemoteCtrlEn | [21 empty] | 0.Load First 1.BatFirst 2.Grid | [14 empty] | Remote setup enable
2101 |  |  |  |  | RemoteCtrlPower | [36 empty] | Remotely set power
2102 |  |  |  |  | Extra AC Power to grid_H | [10 empty] | Extra inverte AC Power to grid High | [10 empty] | For SPA connect inverter | [14 empty] | SPA used
2103 |  |  |  |  | Extra AC Power to grid_L | [10 empty] | Extrainverte AC Power to grid Low | [25 empty] | SPA used
2104 |  |  |  |  | Eextra_today H | [10 empty] | Extra inverter PowerTOUser_Extra today (high) | [10 empty] | R | [10 empty] | 0.1kWh |  |  |  | SPA used
2105 |  |  |  |  | Eextra_today L | [10 empty] | Extra inverter PowerTOUser_Extra today (low) | [10 empty] | R | [10 empty] | 0.1kWh |  |  |  | SPA used
2106 |  |  |  |  | Eextra_total H | [10 empty] | Extra inverter PowerTOUser_Extra total(high) | [21 empty] | 0.1kWh |  |  |  | SPA used
2107 |  |  |  |  | Eextra_total L | [10 empty] | Extra inverter PowerTOUser_Extra total(low) | [21 empty] | 0.1kWh |  |  |  | SPA used
2108 |  |  |  |  | Esystem_today H | [10 empty] | System electric energy today H | [21 empty] | 0.1kWh |  |  |  | SPA used System electric energy today H
2109 |  |  |  |  | Esystem_ today L | [10 empty] | System electric energy today L | [21 empty] | 0.1kWh |  |  |  | SPA used System electric energy today L
2110 |  |  |  |  | Esystem_total H | [10 empty] | System electric energy total H | [21 empty] | 0.1kWh |  |  |  | SPA used System electric energy total H
2111 |  |  |  |  | Esystem_ total L | [10 empty] | System electric energy total L | [21 empty] | 0.1kWh |  |  |  | SPA used System electric energy total L
2112 |  |  |  |  | EACharge_Today_H | [10 empty] | ACCharge energy today | [21 empty] | 0.1kwh |  |  |  | Storage Power
2113 |  |  |  |  | EACharge_Today_L | [10 empty] | ACCharge energy today | [21 empty] | 0.1kwh |  |  |  | Storage Power
2114 |  |  |  |  | EACharge_Total_H | [10 empty] | ACCharge energy total | [21 empty] | 0.1kwh |  |  |  | Storage Power
2115 |  |  |  |  | EACharge_Total_L | [10 empty] | ACCharge energy total | [21 empty] | 0.1kwh |  |  |  | Storage Power
2116 |  |  |  |  | AC charge Power_H | [10 empty] | Grid power to local load | [21 empty] | 0.1kwh |  |  |  | Storage Power
2117 |  |  |  |  | AC charge Power_L | [10 empty] | Grid power to local load | [21 empty] | 0.1kwh |  |  |  | Storage Power
2118 |  |  |  |  | Priority | [10 empty] | 0:Load First 1:Battery First 2:Grid First | [25 empty] | Storage Power
2119 |  |  |  |  | Battery Type | [10 empty] | 0:Lead-acid 1:Lithium battery | [25 empty] | Storage Power
2120 |  |  |  |  | AutoProofreadCMD | [10 empty] | Aging mode | [25 empty] | Storage Power
…… |  |  |  |  | reserved | [36 empty] | reserved
2124 |  |  |  |  | reserved | [36 empty] | reserved
Use for TL-X and TL-XH
3000 |  |  |  |  | Inverter Status | [10 empty] | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: Self-test mode, optional 2: Reserved 3:SysFault module 4: Flash module 5:PVBATOnline module: 6:BatOnline module 7:PVOfflineMode 8:BatOfflineMode The lower 8 bits indicate the machine status (web page display): 0:StandbyStatus; 1:OngridStatus; 2:OffgridStatus; 3:FaultStatus 4:FlashStatus;
3001 |  |  |  |  | Ppv H | [10 empty] | PV total power | [21 empty] | 0.1W
3002 |  |  |  |  | Ppv L
3003 |  |  |  |  | Vpv1 | [10 empty] | PV1 voltage | [21 empty] | 0.1V
3004 |  |  |  |  | Ipv1 | [10 empty] | PV1 input current | [21 empty] | 0.1A
3005 |  |  |  |  | Ppv1 H | [10 empty] | PV1 power | [21 empty] | 0.1W
3006 |  |  |  |  | Ppv1 L
3007 |  |  |  |  | Vpv2 | [10 empty] | PV2 voltage | [21 empty] | 0.1V
3008 |  |  |  |  | Ipv2 | [10 empty] | PV2 input current | [21 empty] | 0.1A
3009 |  |  |  |  | Ppv2 H | [10 empty] | PV2 power | [21 empty] | 0.1W
3010 |  |  |  |  | Ppv2 L
3011 |  |  |  |  | Vpv3 | [10 empty] | PV3 voltage | [21 empty] | 0.1V
3012 |  |  |  |  | Ipv3 | [10 empty] | PV3 input current | [21 empty] | 0.1A
3013 |  |  |  |  | Ppv3 H | [10 empty] | PV3 power | [21 empty] | 0.1W
3014 |  |  |  |  | Ppv3 L
3015 |  |  |  |  | Vpv4 | [10 empty] | PV4 voltage
3016 |  |  |  |  | Ipv4 | [10 empty] | PV4 input current
3017 |  |  |  |  | Ppv4H | [10 empty] | PV4 power
3018 |  |  |  |  | Ppv4L
3019 |  |  |  |  | Psys H | [10 empty] | System output power | [21 empty] | 0.1W
3020 |  |  |  |  | Psys L
3021 |  |  |  |  | Qac H | [10 empty] | reactive power | [21 empty] | 0.1Var
3022 |  |  |  |  | Qac L
3023 |  |  |  |  | Pac H | [10 empty] | Output power | [21 empty] | 0.1W |  |  |  | Output power
3024 |  |  |  |  | Pac L
3025 |  |  |  |  | Fac | [10 empty] | Grid frequency | [21 empty] | 0.01Hz |  |  |  | Grid frequency
3026 |  |  |  |  | Vac1 | [10 empty] | Three/single phase grid voltage | [21 empty] | 0.1V |  |  |  | Three/single phase grid voltage
3027 |  |  |  |  | Iac1 | [10 empty] | Three/single phase grid output current | [21 empty] | 0.1A |  |  |  | Three/single phase grid output current
3028 |  |  |  |  | Pac1 H | [10 empty] | Three/single phase grid output watt VA | [21 empty] | 0.1VA |  |  |  | Three/single phase grid output watt VA
3029 |  |  |  |  | Pac1 L
3030 |  |  |  |  | Vac2 | [10 empty] | Three phase grid voltage | [21 empty] | 0.1V |  |  |  | Three phase grid voltage
3031 |  |  |  |  | Iac2 | [10 empty] | Three phase grid output current | [21 empty] | 0.1A |  |  |  | Three phase grid output current
3032 |  |  |  |  | Pac2 H | [10 empty] | Three phase grid output power | [21 empty] | 0.1VA |  |  |  | Three phase grid output power
3033 |  |  |  |  | Pac2 L
3034 |  |  |  |  | Vac3 | [10 empty] | Three phase grid voltage | [21 empty] | 0.1V |  |  |  | Three phase grid voltage
3035 |  |  |  |  | Iac3 | [10 empty] | Three phase grid output current | [21 empty] | 0.1A |  |  |  | Three phase grid output current
3036 |  |  |  |  | Pac3 H | [10 empty] | Three phase grid output power | [21 empty] | 0.1VA |  |  |  | Three phase grid output power
3037 |  |  |  |  | Pac3 L
3038 |  |  |  |  | Vac_RS | [10 empty] | Three phase grid voltage | [21 empty] | 0.1V
3039 |  |  |  |  | Vac_ST | [10 empty] | Three phase grid voltage | [21 empty] | 0.1V
3040 |  |  |  |  | Vac_TR | [10 empty] | Three phase grid voltage | [21 empty] | 0.1V
3041 |  |  |  |  | Ptouser total H | [10 empty] | Total forward power | [21 empty] | 0.1W |  |  |  | Total forward power
3042 |  |  |  |  | Ptouser total L
3043 |  |  |  |  | Ptogrid total H | [10 empty] | Total reverse power | [21 empty] | 0.1W |  |  |  | Total reverse power
3044 |  |  |  |  | Ptogrid total L
3045 |  |  |  |  | Ptoload total H | [10 empty] | Total load power | [21 empty] | 0.1W |  |  |  | Total load power
3046 |  |  |  |  | Ptoload total L
3047 |  |  |  |  | Time total H | [10 empty] | Work time total | [21 empty] | 0.5s
3048 |  |  |  |  | Time total L
3049 |  |  |  |  | Eac today H | [10 empty] | Today generate energy | [21 empty] | 0.1kWh |  |  |  | Today generate energy
3050 |  |  |  |  | Eac today L
3051 |  |  |  |  | Eac total H | [10 empty] | Total generate energy | [21 empty] | 0.1kWh |  |  |  | Total generate energy
3052 |  |  |  |  | Eac total L
3053 |  |  |  |  | Epv_total H | [10 empty] | PV energy total | [21 empty] | 0.1kWh |  |  |  | PV energy total
3054 |  |  |  |  | Epv_total L
3055 |  |  |  |  | Epv1_today H | [10 empty] | PV1 energy today | [21 empty] | 0.1kWh
3056 |  |  |  |  | Epv1_today L
3057 |  |  |  |  | Epv1_total H | [10 empty] | PV1 energy total | [21 empty] | 0.1kWh
3058 |  |  |  |  | Epv1_total L
3059 |  |  |  |  | Epv2_today H | [10 empty] | PV2 energy today | [21 empty] | 0.1kWh
3060 |  |  |  |  | Epv2_today L
3061 |  |  |  |  | Epv2_total H | [10 empty] | PV2 energy total | [21 empty] | 0.1kWh
3062 |  |  |  |  | Epv2_total L
3063 |  |  |  |  | Epv3_today H | [10 empty] | PV3 energy today | [21 empty] | 0.1kWh
3064 |  |  |  |  | Epv3_today L
3065 |  |  |  |  | Epv3_total H | [10 empty] | PV3 energy total | [21 empty] | 0.1kWh
3066 |  |  |  |  | Epv3_total L
3067 |  |  |  |  | Etouser_today H | [10 empty] | Today energy to user | [21 empty] | 0.1kWh |  |  |  | Today energy to user
3068 |  |  |  |  | Etouser_today L
3069 |  |  |  |  | Etouser_total H | [10 empty] | Total energy to user | [21 empty] | 0.1kWh |  |  |  | Total energy to user
3070 |  |  |  |  | Etouser_total L
3071 |  |  |  |  | Etogrid_today H | [10 empty] | Today energy to grid | [21 empty] | 0.1kWh |  |  |  | Today energy to grid
3072 |  |  |  |  | Etogrid_today L
3073 |  |  |  |  | Etogrid_total H | [10 empty] | Total energy to grid | [21 empty] | 0.1kWh |  |  |  | Total energy to grid
3074 |  |  |  |  | Etogrid_total L
3075 |  |  |  |  | Eload_today H | [10 empty] | Today energy of user load | [21 empty] | 0.1kWh |  |  |  | Today energy of user load
3076 |  |  |  |  | Eload_today L
3077 |  |  |  |  | Eload_total H | [10 empty] | Total energy of user load | [21 empty] | 0.1kWh |  |  |  | Total energy of user load
3078 |  |  |  |  | Eload_total L
3079 |  |  |  |  | Epv4_today H | [10 empty] | PV4 energy today | [21 empty] | 0.1kWh
3080 |  |  |  |  | Epv4_today L
3081 |  |  |  |  | Epv4_total H | [10 empty] | PV4 energy total | [21 empty] | 0.1kWh
3082 |  |  |  |  | Epv4_total L
3083 |  |  |  |  | Epv_today H | [10 empty] | PV energy today | [21 empty] | 0.1kWh
3084 |  |  |  |  | Epv_today L
3085 |  |  |  |  | Reserved
3086 |  |  |  |  | DeratingMode | [10 empty] | Inverter derating mode | [10 empty] | R | [14 empty] | Appendix table 1
3087 |  |  |  |  | ISO | [10 empty] | PV ISO value | [21 empty] | 1KΩ
3088 |  |  |  |  | DCI_R | [10 empty] | R DCI Curr | [21 empty] | 0.1mA
3089 |  |  |  |  | DCI_S | [10 empty] | S DCI Curr | [21 empty] | 0.1mA
3090 |  |  |  |  | DCI_T | [10 empty] | T DCI Curr | [21 empty] | 0.1mA
3091 |  |  |  |  | GFCI | [10 empty] | GFCI Curr | [21 empty] | 1mA
3092 |  |  |  |  | Bus Voltage | [10 empty] | total bus voltage | [21 empty] | 0.1V
3093 |  |  |  |  | Temp1 | [10 empty] | Inverter temperature | [21 empty] | 0.1℃
3094 |  |  |  |  | Temp2 | [10 empty] | The inside IPM in inverter temperature | [21 empty] | 0.1℃
3095 |  |  |  |  | Temp3 | [10 empty] | Boost temperature | [21 empty] | 0.1℃
3096 |  |  |  |  | Temp4 | [10 empty] | Reserved | [21 empty] | 0.1℃
3097 |  |  |  |  | Temp5 | [10 empty] | Commmunication broad temperature | [21 empty] | 0.1℃
3098 |  |  |  |  | P Bus Voltage | [10 empty] | P Bus inside Voltage | [21 empty] | 0.1V
3099 |  |  |  |  | N Bus Voltage | [10 empty] | N Bus inside Voltage | [21 empty] | 0.1V
3100 |  |  |  |  | IPF | [10 empty] | Inverter output PF now | [25 empty] | 0-20000
3101 |  |  |  |  | RealOPPercent | [10 empty] | Real Output power Percent | [21 empty] | 1% |  |  |  | 1~100
3102 |  |  |  |  | OPFullwatt H | [10 empty] | Output Maxpower Limited | [21 empty] | 0.1W |  |  |  | Output Maxpower Limited
3103 |  |  |  |  | OPFullwatt L
3104 |  |  |  |  | StandbyFlag | [10 empty] | Inverter standby flag | [21 empty] | bitfield |  |  |  | bit0:turn off Order bit1:PV Low bit2:AC Volt/Freq out of scope bit3~bit7:Re served
3105 |  |  |  |  | Fault Maincode | [10 empty] | Inverter fault maincode
3106 |  |  |  |  | Warn Maincode | [10 empty] | Inverter Warning maincode
3107 |  |  |  |  | Fault Subcode | [10 empty] | Inverter fault subcode | [21 empty] | bitfield
3108 |  |  |  |  | Warn Subcode | [10 empty] | Inverter Warning subcode | [21 empty] | bitfield
3109 | [37 empty] | bitfield
3110 | [37 empty] | bitfield
3111 |  |  |  |  | uwPresentFFTValue [CHANNEL_A] | [10 empty] | PresentFFTValue [C HANNEL_A] | [21 empty] | bitfield
3112 |  |  |  |  | bAfciStatus | [10 empty] | AFCI Status | [25 empty] | 0:waiting state 1:self-check 2:Detection of arcing state 3:fault state 4:update state
3113 |  |  |  |  | uwStrength[CHANN EL_A] | [10 empty] | AFCI Strength[CHANNEL_ A]
3114 |  |  |  |  | uwSelfCheckValue[ CHANNEL_A] | [10 empty] | AFCI SelfCheck[CHANNEL _A]
3115 |  |  |  |  | inv start delay time | [10 empty] | inv start delay time | [21 empty] | 1S |  |  |  | inv start delay time
3116 |  |  |  |  | Time total H | [32 empty] | 0.5S
3117 |  |  |  |  | Time total L
3118 |  |  |  |  | BDC_OnOffState | [10 empty] | BDC connect state | [25 empty] | 0:No BDC Connect 1:BDC1 Connect 2:BDC2 Connect 3:BDC1+BDC 2 Connect
3119 |  |  |  |  | DryContactState | [10 empty] | Current status of DryContact | [25 empty] | Current status of DryContact 0: turn off; 1: turn on;
3120 |  |  |  |  | Reserved
3121 |  |  |  |  | Pself H | [10 empty] | self-use power | [21 empty] | 0.1W
3122 |  |  |  |  | Pself L
3123 |  |  |  |  | Esys_today H | [10 empty] | System energy today | [21 empty] | 0.1kwh
3124 |  |  |  |  | Esys_today L
3125 |  |  |  |  | Edischr_today H | [10 empty] | Today discharge energy | [21 empty] | 0.1kWh |  |  |  | Today discharge energy
3126 |  |  |  |  | Edischr_today L
3127 |  |  |  |  | Edischr_total H | [10 empty] | Total discharge energy | [21 empty] | 0.1kWh |  |  |  | Total discharge energy
3128 |  |  |  |  | Edischr_total L
3129 |  |  |  |  | Echr_today H | [10 empty] | Charge energy today | [21 empty] | 0.1kWh |  |  |  | Charge energy today
3130 |  |  |  |  | Echr_today L
3131 |  |  |  |  | Echr_total H | [10 empty] | Charge energy total | [21 empty] | 0.1kWh |  |  |  | Charge energy total
3132 |  |  |  |  | Echr_total L
3133 |  |  |  |  | Eacchr_today H | [10 empty] | Today energy of AC charge | [21 empty] | 0.1kWh |  |  |  | Today energy of AC charge
3134 |  |  |  |  | Eacchr_today L
3135 |  |  |  |  | Eacchr_total H | [10 empty] | Total energy of AC charge | [21 empty] | 0.1kWh |  |  |  | Total energy of AC charge
3136 |  |  |  |  | Eacchr_total L
3137 |  |  |  |  | Esys_total H | [10 empty] | Total energy of system output | [21 empty] | 0.1kWh
3138 |  |  |  |  | Esys_total L
3139 |  |  |  |  | Eself_today H | [10 empty] | Today energy of Self output | [21 empty] | 0.1kWh
3140 |  |  |  |  | Eself_today L
3141 |  |  |  |  | Eself_total H | [10 empty] | Total energy of Self output | [21 empty] | 0.1kWh
3142 |  |  |  |  | Eself_ total L
3143 |  |  |  |  | Reserved
3144 |  |  |  |  | Priority | [10 empty] | Word Mode | [25 empty] | 0:LoadFirst 1:BatteryFirs t 2:GridFirst
3145 |  |  |  |  | EPS Fac | [10 empty] | UPS frequency | [21 empty] | 0.01Hz
3146 |  |  |  |  | EPS Vac1 | [10 empty] | UPS phase R output voltage | [21 empty] | 0.1V
3147 |  |  |  |  | EPS Iac1 | [10 empty] | UPS phase R output current | [21 empty] | 0.1A
3148 |  |  |  |  | EPS Pac1 H | [10 empty] | UPS phase R output power | [21 empty] | 0.1VA
3149 |  |  |  |  | EPS Pac1 L
3150 |  |  |  |  | EPS Vac2 | [10 empty] | UPS phase S output voltage | [21 empty] | 0.1V
3151 |  |  |  |  | EPS Iac2 | [10 empty] | UPS phase S output current | [21 empty] | 0.1A
3152 |  |  |  |  | EPS Pac2 H | [10 empty] | UPS phase S output power | [21 empty] | 0.1VA
3153 |  |  |  |  | EPS Pac2 L
3154 |  |  |  |  | EPS Vac3 | [10 empty] | UPS phase T output voltage | [21 empty] | 0.1V
3155 |  |  |  |  | EPS Iac3 | [10 empty] | UPS phase T output current | [21 empty] | 0.1A
3156 |  |  |  |  | EPS Pac3 H | [10 empty] | UPS phase T output power | [21 empty] | 0.1VA
3157 |  |  |  |  | EPS Pac3 L
3158 |  |  |  |  | EPS Pac H | [10 empty] | UPS output power | [21 empty] | 0.1VA
3159 |  |  |  |  | EPS Pac L
3160 |  |  |  |  | Loadpercent | [10 empty] | Load percent of UPS ouput | [21 empty] | 0.1%
3161 |  |  |  |  | PF | [10 empty] | Power factor | [21 empty] | 0.1
3162 |  |  |  |  | DCV | [10 empty] | DC voltage | [21 empty] | 1mV
3163 |  |  |  |  | Reserved
3164 |  |  |  |  | NewBdcFlag | [10 empty] | Whether to parse BDC data separately | [25 empty] | 0:Don't need 1:need
3165 |  |  |  |  | BDCDeratingMode | [10 empty] | Battery derating mode | [10 empty] | R | [14 empty] | Appendix table 2
3166 |  |  |  |  | SysState_Mode | [10 empty] | System work State and mode The upper 8 bits indicate the mode; 0:No charge and discharge; 1:charge; 2:Discharge; The lower 8 bits represent the status; 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3:FlashStatus; | [25 empty] | BDC1
3167 |  |  |  |  | FaultCode | [10 empty] | Storge device fault code
3168 |  |  |  |  | WarnCode | [10 empty] | Storge device warning code
3169 |  |  |  |  | Vbat | [10 empty] | Battery voltage | [21 empty] | 0.01V
3170 |  |  |  |  | Ibat | [10 empty] | Battery current | [21 empty] | 0.1A
3171 |  |  |  |  | SOC | [10 empty] | State of charge Capacity | [21 empty] | 1%
3172 |  |  |  |  | Vbus1 | [10 empty] | Total BUS voltage | [21 empty] | 0.1V
3173 |  |  |  |  | Vbus2 | [10 empty] | On the BUS voltage | [21 empty] | 0.1V
3174 |  |  |  |  | Ibb | [10 empty] | BUCK-BOOST Current | [21 empty] | 0.1A
3175 |  |  |  |  | Illc | [10 empty] | LLC Current | [21 empty] | 0.1A
3176 |  |  |  |  | TempA | [10 empty] | Temperture A | [21 empty] | 0.1℃
3177 |  |  |  |  | TempB | [10 empty] | Temperture B | [21 empty] | 0.1℃
3178 |  |  |  |  | Pdischr H | [10 empty] | Discharge power | [21 empty] | 0.1W
3179 |  |  |  |  | Pdischr L
3180 |  |  |  |  | Pchr H | [10 empty] | Charge power | [21 empty] | 0.1W
3181 |  |  |  |  | Pchr L
3182 |  |  |  |  | Edischr_total H | [10 empty] | Discharge total energy of storge device | [21 empty] | 0.1kWh
3183 |  |  |  |  | Edischr_total L
3184 |  |  |  |  | Echr_total H | [10 empty] | Charge total energy of storge device | [21 empty] | 0.1kWh
3185 |  |  |  |  | Echr_total L
3186 |  |  |  |  | Reserved
3187 |  |  |  |  | BDC1_Flag | [10 empty] | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code
3188 |  |  |  |  | Vbus2 | [10 empty] | Lower BUS voltage | [21 empty] | 0.1V
3189 |  |  |  |  | BmsMaxVoltCellNo | [10 empty] | BmsMaxVoltCellNo
3190 |  |  |  |  | BmsMinVoltCellNo | [10 empty] | BmsMinVoltCellNo
3191 |  |  |  |  | BmsBatteryAvgTem p | [10 empty] | BmsBatteryAvgTem p
3192 |  |  |  |  | BmsMaxCellTemp | [10 empty] | BmsMaxCellTemp | [21 empty] | 0.1°C
3193 |  |  |  |  | BmsBatteryAvgTem p | [10 empty] | BmsBatteryAvgTem p | [21 empty] | 0.1°C
3194 |  |  |  |  | BmsMaxCellTemp | [10 empty] | BmsMaxCellTemp
3195 |  |  |  |  | BmsBatteryAvgTem p | [10 empty] | BmsBatteryAvgTem p
3196 |  |  |  |  | BmsMaxSOC | [10 empty] | BmsMaxSOC | [21 empty] | 1%
3197 |  |  |  |  | BmsMinSOC | [10 empty] | BmsMinSOC | [21 empty] | 1%
3198 |  |  |  |  | ParallelBatteryNum | [10 empty] | ParallelBatteryNum
3199 |  |  |  |  | BmsDerateReason | [10 empty] | BmsDerateReason
3200 |  |  |  |  | BmsGaugeFCC（Ah） | [10 empty] | BmsGaugeFCC（Ah）
3201 |  |  |  |  | BmsGaugeRM（Ah） | [10 empty] | BmsGaugeRM（Ah）
3202 |  |  |  |  | BmsError | [10 empty] | BMS Protect1
3203 |  |  |  |  | BmsWarn | [10 empty] | BMSWarn1
3204 |  |  |  |  | BmsFault | [10 empty] | BMS Fault1
3205 |  |  |  |  | BmsFault2 | [10 empty] | BMS Fault2
3206 |  |  |  |  | Reserved
3207 |  |  |  |  | Reserved
3208 |  |  |  |  | Reserved
3209 |  |  |  |  | Reserved
3210 |  |  |  |  | BatIsoStatus | [10 empty] | Battery ISO detection status | [25 empty] | 0:Not detected 1:Detection completed
3211 |  |  |  |  | BattNeedChargeReq uestFlag | [10 empty] | battery work request | [25 empty] | bit0:1:Prohi bit charging,0:A llow the charging bit1:1:Enabl e strong charge,0:dis able strong charge bit2:1:Enabl e strong charge2 0:disable strong charge 2 bit8:1: Discharge is prohibited, 0:allow discharge bit9:1:Turn on power reduction 0:turn off power reduction
3212 |  |  |  |  | BMS_Status | [10 empty] | battery working status | [10 empty] | R | [14 empty] | 0: dormancy 1:Charge 2:Discharge 3:free 4:standby 5:Soft start 6:fault 7:update
3213 |  |  |  |  | BmsError2 | [10 empty] | BMS Protect2 | [10 empty] | R | [10 empty] | 1
3214 |  |  |  |  | BmsWarn2 | [10 empty] | BMS Warn2 | [10 empty] | R | [10 empty] | 1
3215 |  |  |  |  | BMS_SOC | [10 empty] | BMS SOC | [10 empty] | R | [10 empty] | 1%
3216 |  |  |  |  | BMS_BatteryVolt | [10 empty] | BMS BatteryVolt | [10 empty] | R | [10 empty] | 0.01V
3217 |  |  |  |  | BMS_BatteryCurr | [10 empty] | BMS BatteryCurr | [10 empty] | R | [10 empty] | 0.01A
3218 |  |  |  |  | BMS_BatteryTemp | [10 empty] | battery cell maximum temperature | [10 empty] | R | [10 empty] | 0.1℃
3219 |  |  |  |  | BMS_MaxCurr | [10 empty] | Maximum charging current | [10 empty] | R | [10 empty] | 0.01A
3220 |  |  |  |  | BMS_MaxDischrCur r | [10 empty] | Maximum discharge current | [10 empty] | R | [10 empty] | 0.01A
3221 |  |  |  |  | BMS_CycleCnt | [10 empty] | BMSCycleCnt | [10 empty] | R | [10 empty] | 1
3222 |  |  |  |  | BMS_SOH | [10 empty] | BMS SOH | [10 empty] | R | [10 empty] | 1
3223 |  |  |  |  | BMS_ChargeVoltLi mit | [10 empty] | Battery charging voltage limit value | [10 empty] | R | [10 empty] | 0.01V
3224 |  |  |  |  | BMS_DischargeVolt Limit | [10 empty] | Battery discharge voltage limit value
3225 |  |  |  |  | Bms Warn3 | [10 empty] | BMS Warn 3 | [10 empty] | R | [10 empty] | 1
3226 |  |  |  |  | Bms Error3 | [10 empty] | BMS Protect3 | [10 empty] | R | [10 empty] | 1
3227 |  |  |  |  | Reserved
3228 |  |  |  |  | Reserved
3229 |  |  |  |  | Reserved
3230 |  |  |  |  | BMSSingleVoltMax | [10 empty] | BMS Battery SingleVoltMax | [10 empty] | R | [10 empty] | 0.001V
3231 |  |  |  |  | BMSSingleVoltMin | [10 empty] | BMS Battery SingleVoltMin | [10 empty] | R | [10 empty] | 0.001V
3232 |  |  |  |  | BatLoadVolt | [10 empty] | Battery LoadVolt | [10 empty] | R | [10 empty] | 0.01V |  |  |  | [0,650.00]
3233
3234 |  |  |  |  | Debug data1 | [10 empty] | Debug data1 | [10 empty] | R
3235 |  |  |  |  | Debug data2 | [10 empty] | Debug data2 | [10 empty] | R
3236 |  |  |  |  | Debug data3 | [10 empty] | Debug data3 | [10 empty] | R
3237 |  |  |  |  | Debug data4 | [10 empty] | Debug data4 | [10 empty] | R
3238 |  |  |  |  | Debug data5 | [10 empty] | Debug data5 | [10 empty] | R
3239 |  |  |  |  | Debug data6 | [10 empty] | Debug data6 | [10 empty] | R
3240 |  |  |  |  | Debug data7 | [10 empty] | Debug data7 | [10 empty] | R
3241 |  |  |  |  | Debug data8 | [10 empty] | Debug data8 | [10 empty] | R
3242 |  |  |  |  | Debug data9 | [10 empty] | Debug data9 | [10 empty] | R
3243 |  |  |  |  | Debug data10 | [10 empty] | Debug data10 | [10 empty] | R
3244 |  |  |  |  | Debug data10 | [10 empty] | Debug data10 | [10 empty] | R
3245 |  |  |  |  | Debug data12 | [10 empty] | Debug data12 | [10 empty] | R
3246 |  |  |  |  | Debug data13 | [10 empty] | Debug data13 | [10 empty] | R
3247 |  |  |  |  | Debug data14 | [10 empty] | Debug data14 | [10 empty] | R
3248 |  |  |  |  | Debug data15 | [10 empty] | Debug data15 | [10 empty] | R
3249 |  |  |  |  | Debug data16 | [10 empty] | Debug data16 | [10 empty] | R
3250 |  |  |  |  | Pex1H | [10 empty] | PV inverter 1 output power H | [10 empty] | R | [10 empty] | 0.1W
3251 |  |  |  |  | Pex1L | [10 empty] | PV inverter 1 output power L | [10 empty] | R | [10 empty] | 0.1W
3252 |  |  |  |  | Pex2H | [10 empty] | PV inverter 2 output power H | [10 empty] | R | [10 empty] | 0.1W
3253 |  |  |  |  | Pex2L | [10 empty] | PV inverter 2 output power L | [10 empty] | R | [10 empty] | 0.1W
3254 |  |  |  |  | Eex1TodayH | [10 empty] | PV inverter 1 energy Today H | [10 empty] | R | [10 empty] | 0.1kWh
3255 |  |  |  |  | Eex1TodayL | [10 empty] | PV inverter 1 energy Today L | [10 empty] | R | [10 empty] | 0.1kWh
3256 |  |  |  |  | Eex2TodayH | [10 empty] | PV inverter 2 energy Today H | [10 empty] | R | [10 empty] | 0.1kWh
3257 |  |  |  |  | Eex2TodayL | [10 empty] | PV inverter 2 energy Today L | [10 empty] | R | [10 empty] | 0.1kWh
3258 |  |  |  |  | Eex1TotalH | [10 empty] | PV inverter 1 energy Total H | [10 empty] | R | [10 empty] | 0.1kWh
3259 |  |  |  |  | Eex1TotalL | [10 empty] | PV inverter 1 energy Total L | [10 empty] | R | [10 empty] | 0.1kWh
3260 |  |  |  |  | Eex2TotalH | [10 empty] | PV inverter 2 energy Total H | [10 empty] | R | [10 empty] | 0.1kWh
3261 |  |  |  |  | Eex2TotalL | [10 empty] | PV inverter 2 energy Total L | [10 empty] | R | [10 empty] | 0.1kWh
3262 |  |  |  |  | uwBatNo | [10 empty] | battery pack number | [10 empty] | R | [14 empty] | BDC reports update every 15 minutes
3263 |  |  |  |  | BatSerialNum1 | [10 empty] | Battery pack serial numberSN[0]SN[1] | [10 empty] | R | [14 empty] | BDC reports update every 15 minutes
3264 |  |  |  |  | BatSerialNum2 | [10 empty] | Battery pack serial numberSN[2]SN[3] | [10 empty] | R
3265 |  |  |  |  | BatSerialNum3 | [10 empty] | Battery pack serial numberSN[4]SN[5] | [10 empty] | R
3266 |  |  |  |  | BatSerialNum4 | [10 empty] | Battery pack serial numberSN[6]SN[7] | [10 empty] | R
3267 |  |  |  |  | BatSerialNum5 | [10 empty] | Battery pack serial numberSN[8]SN[9] | [10 empty] | R
3268 |  |  |  |  | BatSerialNum6 | [10 empty] | Battery pack serial numberSN[10]SN[1 1] | [10 empty] | R
3269 |  |  |  |  | BatSerialNum7 | [10 empty] | Battery pack serial numberSN[12]SN[1 3] | [10 empty] | R
3270 |  |  |  |  | BatSerialNum8 | [10 empty] | Battery pack serial numberSN[14]SN[1 5] | [10 empty] | R
…… |  |  |  |  | Reserve | [10 empty] | Reserve
3277 |  |  |  |  | bInvSnNumberFlag | [10 empty] | inverter SN number flag | [10 empty] | R | [14 empty] | 0:other 1:10 bit SN 2:16 bit SN 3:21 bit SN
3278 |  |  |  |  | bBatterySnNumber Flag | [10 empty] | battery SN number flag | [10 empty] | R | [14 empty] | Bit0-7: BDC1: 0:other 1:10 bit SN 2:16 bit SN 3:21 bit SN Bit8-15: BDC2: 0:other 1:10 bit SN 2:16 bit SN 3:21 bit SN
3279 |  |  |  |  | bBoxSnNumberFlag | [10 empty] | inverter SN number flag | [10 empty] | R | [14 empty] | 0:other 1:10 bit SN 2:16 bit SN 3:21 bit SN
3280 |  |  |  |  | bClrTodayDataFlag | [10 empty] | Clear day data flag | [10 empty] | R | [14 empty] | Data of the current day that the server determines whether to clear. 0:not cleared. 1: Clear.
3281 |  |  |  |  | ubBypassStatus | [10 empty] | Backup box bypass switch status | [10 empty] | R | [14 empty] | Value: 0:Off 1:On (Reserved)
3282 |  |  |  |  | ubWorkMode | [10 empty] | Backup box work mode | [10 empty] | R | [14 empty] | Value: 0:Offgrid ; 1:Ongrid; 2:Generator
3283 |  |  |  |  | ubFanStatus | [10 empty] | Backup box fan status | [10 empty] | R | [14 empty] | Value: 0:Off 1:On
3284 |  |  |  |  | uwErrorCode | [10 empty] | Backup box error code | [10 empty] | R | [14 empty] | Value:700-8 00
3285 |  |  |  |  | uwWarnCode | [10 empty] | Backup box warning code | [10 empty] | R | [14 empty] | Value:700-8 00
3286 |  |  |  |  | bNtcTemp | [10 empty] | Backup box temprature | [10 empty] | R | [10 empty] | 1℃ |  |  |  | Value:-40-10 0 Type:Int8
3287 |  |  |  |  | uwGridVolt | [10 empty] | Backup box grid voltage | [10 empty] | R | [10 empty] | 0.1V |  |  |  | Type:Uint16
3288 |  |  |  |  | uwGridCurr | [10 empty] | Backup box grid current | [10 empty] | R | [10 empty] | 0.1A |  |  |  | Type:Uint16
3289 |  |  |  |  | dGridWatt_H | [10 empty] | Backup box grid power | [10 empty] | R | [10 empty] | 0.1W |  |  |  | Type:Int32
3290 |  |  |  |  | dGridWatt_L
3291 |  |  |  |  | uwGridFreq | [10 empty] | Backup box grid frequency | [10 empty] | R | [10 empty] | 0.01Hz |  |  |  | Type:Uint16
3292 |  |  |  |  | uwGenVolt | [10 empty] | Backup box generator voltage | [10 empty] | R | [10 empty] | 0.1V |  |  |  | Type:Uint16
3293 |  |  |  |  | uwGenCurr | [10 empty] | Backup box generator current | [10 empty] | R | [10 empty] | 0.1A |  |  |  | Type:Uint16
3294 |  |  |  |  | DGenWatt_H | [10 empty] | Backup box generator power | [10 empty] | R | [10 empty] | 0.1W |  |  |  | Type:Int32
3295 |  |  |  |  | DGenWatt_L
3296 |  |  |  |  | uwGenFreq | [10 empty] | Backup box generator frequency | [10 empty] | R | [10 empty] | 0.01Hz |  |  |  | Type:Uint16
3297 |  |  |  |  | dLoadWatt_H | [10 empty] | Backup box load power | [10 empty] | R | [10 empty] | 0.1W |  |  |  | Type:Uint32
3298 |  |  |  |  | dLoadWatt_L
3299 |  |  |  |  | uwFirmwareCode_ H | [10 empty] | Backup box firmware code | [10 empty] | R | [14 empty] | Value: 4 characters Type: ASCII
3300 |  |  |  |  | uwFirmwareCode_L
3301 |  |  |  |  | ubFirmwareVersion | [10 empty] | Backup box firmware version | [10 empty] | R | [14 empty] | Type:Uint8
3302 |  |  |  |  | uwSerialNum0 | [10 empty] | Backup box serial number | [10 empty] | R | [14 empty] | Value: 30 characters Type:ASCII
3303 |  |  |  |  | uwSerialNum1
3304 |  |  |  |  | uwSerialNum2
3305 |  |  |  |  | uwSerialNum3
3306 |  |  |  |  | uwSerialNum4
3307 |  |  |  |  | uwSerialNum5
3308 |  |  |  |  | uwSerialNum6
3309 |  |  |  |  | uwSerialNum7
3310 |  |  |  |  | uwSerialNum8
3311 |  |  |  |  | uwSerialNum9
3312 |  |  |  |  | uwSerialNum10
3313 |  |  |  |  | uwSerialNum11
3314 |  |  |  |  | uwSerialNum12
3315 |  |  |  |  | uwSerialNum13
3316 |  |  |  |  | uwSerialNum14
3317 |  |  |  |  | uwGridVoltS | [10 empty] | Backup box S phase grid voltage(for XH model) | [10 empty] | R | [10 empty] | 0.1V
3318 |  |  |  |  | uwGridVoltT | [10 empty] | Backup box T phase grid voltage(for XH model) | [10 empty] | R | [10 empty] | 0.1V
3319 |  |  |  |  | uwGridFreqS | [10 empty] | Backup box S phase grid frequency(for XH model) | [10 empty] | R | [10 empty] | 0.01Hz
3320 |  |  |  |  | bBoxConnectFlag | [10 empty] | Backup box communication status (for for GW server) | [10 empty] | R | [14 empty] | 0: Abnormal 1:Normal
3321 |  |  |  |  | bBoxDataUploadFla g | [10 empty] | Backup box Upload flag(for GW server) | [10 empty] | R | [14 empty] | 0:No 1:Yes
3322 |  |  |  |  | MeterConnectFlag | [10 empty] | Ankeri meter connection status | [10 empty] | R | [14 empty] | 0: Invalid 1: Normal
3323 |  |  |  |  | SYNInstalledFlag | [10 empty] | The backup box installation flag determines whether backup box is installed based on the communication between M3 and backup box | [10 empty] | R | [14 empty] | 0: backup box is not installed 1: backup box is installed
3324 |  |  |  |  | BoxUnbalanceCurre nt | [10 empty] | Backup box unbalance current | [10 empty] | R | [10 empty] | 0.1A
…… |  |  |  |  | Reserve | [10 empty] | Reserve
3342 |  |  |  |  | InvRelayStatus | [10 empty] | Backup box inv relay status | [10 empty] | R | [14 empty] | 0:software not support reading or box communicat ion abnormal 1:open 2:close
3343 |  |  |  |  | GenvRelayStatus | [10 empty] | Generator relay status | [10 empty] | R | [14 empty] | 0:software not support reading or box communicat ion abnormal 1:open 2:close
…… |  |  |  |  | Reserve | [10 empty] | Reserve
3410 |  |  |  |  | ErrorBit1 | [10 empty] | Error bit1
3411 |  |  |  |  | ErrorBit2 | [10 empty] | Error bit2
3412 |  |  |  |  | ErrorBit3 | [10 empty] | Error bit3
3413 |  |  |  |  | ErrorBit4 | [10 empty] | Error bit4
3414 |  |  |  |  | WarningBit1 | [10 empty] | Warning bit1
3415 |  |  |  |  | WarningBit2 | [10 empty] | Warning bit2
3416 |  |  |  |  | WarningBit3 | [10 empty] | Warning bit3
3417 |  |  |  |  | WarningBit4 | [10 empty] | Warning bit4
BDC and BMS information (support up to 10 PARALLEL BDCS)
4000 ~410 7. |  |  |  |  | 1 | [10 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4108 ~421 5. |  |  |  |  | 2 | [10 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
…… | [15 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4864 ~497 1. |  |  |  |  | 9 | [10 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4972 ~507 9. |  |  |  |  | 10 | [10 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
Battery module information (support up to 64 parallel BDC)（Special for APX）
5080 |  |  |  |  | BatSysState | [7 empty] | System working state | [13 empty] | R | [14 empty] | 0:initialize; 1:standby; 2:charge; 3:discharge; 4:shutdown; 5:fault; 6:update;
5081 |  |  |  |  | BatSOC | [21 empty] | R | [10 empty] | 1% |  |  |  | Bit 15-8: Mapping SOC[0,100] Bit7-0: SOC[0,100]
5082 |  |  |  |  | BatSOH | [21 empty] | R | [10 empty] | 1% |  |  |  | bit7: 0:Represent available 1:Represent need to scrap Bit6-bit0: SOH value[0,100]
5083 |  |  |  |  | BatVolt | [7 empty] | Total internal voltage of battery system | [13 empty] | R | [10 empty] | 0.1V |  |  |  | [0,1500.0V]
5084 |  |  |  |  | BatCurrent | [7 empty] | Battery system current | [13 empty] | R | [10 empty] | 0.1A |  |  |  | [-1000.0,100 0.0A]
5085 |  |  |  |  | BatPower | [7 empty] | Charge and discharge power | [13 empty] | R | [10 empty] | 1W |  |  |  | [-32000,320 00W]
5086 |  |  |  |  | BatTotalDischar eElectric | [7 empty] | Cumulative discharge energy | [13 empty] | R | [10 empty] | 0.1kWh |  |  |  | [0,2000000. 0 kwH]
5087
5088 |  |  |  |  | BatMaxCellVolt | [7 empty] | Maximum cell voltage | [13 empty] | R | [10 empty] | 0.001V |  |  |  | [0,6.000V]
5089 |  |  |  |  | BatMinCellVolt | [7 empty] | Minimum cell voltage | [13 empty] | R | [10 empty] | 0.001V |  |  |  | [0,6.000V]
5090 |  |  |  |  | BatMaxTemp | [7 empty] | Maximum battery temperature | [13 empty] | R | [10 empty] | 0.1℃ |  |  |  | [-40.0,125.0 ℃]
5091 |  |  |  |  | BatMinTemp | [7 empty] | Minimum battery temperature | [13 empty] | R | [10 empty] | 0.1℃ |  |  |  | [-40.0,125.0 ℃]
5092 |  |  |  |  | BatMaxLimitCh argeCurrent | [7 empty] | Maximum allowable charging current | [13 empty] | R | [10 empty] | 0.1A |  |  |  | [0,1000.0A]
5093 |  |  |  |  | BatMaxLimitDis chargeCurrent | [7 empty] | Maximum allowable discharge current | [13 empty] | R | [10 empty] | 0.1A |  |  |  | [0,1000.0A]
5094 |  |  |  |  | BatBalanceStat e | [7 empty] | Battery balance state Bit15-bit8: 0: Balancing is not detected. 1: The bottom end detects the need for balancing and updates the balancing time; 2: The top detects the need for balancing and updates the balancing time; 3: The charging terminal detects the need for balancing, and updates the balancing time; 4: Even channels are balanced when parity balance is limited; 5: Limit the parity balance in the case of odd channels to perform balancing; 6: The balance is not completed, but the balance is closed; 7: Parity channels are balanced without limiting parity balance; 8: The balance is complete | [13 empty] | R | [14 empty] | Balance time Bit7-bit0: Unit h; Data type uint8. Balancing time longer than 255 is shown as 255 hours
5095 |  |  |  |  | BatCellCapacity | [7 empty] | Effective cell capacity | [13 empty] | R | [10 empty] | 0.1Ah |  |  |  | [0,5000.0Ah ]
5096 |  |  |  |  | BatRealSOC | [7 empty] | Real SOC/ Number of the battery module | [13 empty] | R | [10 empty] | 1% |  |  |  | Bit15~bit13: Indicates the number of the BDC group to which it belongs. Range[1-4] Bit12~bit8: Indicates the number of the battery module in the BDC group. Range[1-21] Bit7~bit0: Real SOC. Range [0,100]
5097 |  |  |  |  | BatFaultCode | [21 empty] | R
5098 |  |  |  |  | BatWarningCod e | [21 empty] | R
5099 |  |  |  |  | BatSubCode | [7 empty] | Charge and discharge flag / Fault subcode / Warning subcode | [13 empty] | R | [14 empty] | Charge and discharge flag Bit0:Enable charging Bit1:Dischar ge enabled Bit2-7:reser ved Fault subcode / Warning subcode Bit8-11:War ning subcode bit12-15:Fau lt subcode
5100 |  |  |  |  | BatTotalCharge Electric | [7 empty] | Cumulative charge energy | [13 empty] | R | [10 empty] | 0.1kwh |  |  |  | [0~4294967 29.5kwh]
5101
5102 |  |  |  |  | BatTotalDischar ge Capacity | [7 empty] | Cumulative discharge capacity | [13 empty] | R | [10 empty] | 0.01Ah |  |  |  | [0~4294967 2.95Ah]
5103
5104 |  |  |  |  | BatTotalCharge Capacity | [7 empty] | Cumulative charge capacity | [13 empty] | R | [10 empty] | 0.01Ah |  |  |  | [0~4294967 2.95Ah]
5105
5106 |  |  |  |  | BatMinCellCapa city | [7 empty] | Minimum cell capacity | [13 empty] | R | [10 empty] | 0.1Ah |  |  |  | [0,6553.5 Ah]
5107 |  |  |  |  | BatAHIntegral Value | [7 empty] | AH integral value of the battery | [13 empty] | R | [10 empty] | 0.1Ah |  |  |  | [0,6553.5 Ah]
5108 |  |  |  |  | BatCyclesNumb er | [7 empty] | Number of charge and discharge cycles | [13 empty] | R | [10 empty] | 0.1 |  |  |  | [0,6553.5 Cyc]
5109 |  |  |  |  | BatInternalStat e | [21 empty] | R | [14 empty] | Bit15-8:Inter nal short-circuit condition Bit7-0:Batte ry SOX correction status
5110 |  |  |  |  | BDCDerating Mode | [21 empty] | R | [10 empty] | [0,32] |  |  |  | No 111 distinguish Charge/ Discharge 0: No derating 1: Fault
17: Maximum battery discharge current 18: Battery discharge is enabled 19: The BUS voltage is too high 20: Discharge NTC high temperature 21: Discharge system alarm is generated 22: Discharge upper computer Settings 23-32: Reserved
5111- 5119. |  |  |  |  | Reserved
5120-5 159. |  |  |  |  | Battery module 2 | [28 empty] | Reference 5080 to 5119 for a total of 40 registers description
5160-5 199. |  |  |  |  | Battery module 3 | [28 empty] | Reference 5080 to 5119 for a total of 40 registers description
5080+( N-1)*4 0---- 5119+( N-1)*4 0 |  |  |  |  | Battery module N(supports up to 64 battery modules)
8000—9000 for business Storage Power
8000 |  |  |  |  | Vpv9 | [7 empty] | PV9 voltage | [20 empty] | 0.1V
8001 |  |  |  |  | PV9Curr | [7 empty] | PV9 input current | [20 empty] | 0.1A
8002 |  |  |  |  | Ppv9 H | [7 empty] | PV9 input power(high) | [20 empty] | 0.1W
8003 |  |  |  |  | Ppv9 L | [7 empty] | PV9 input power(low) | [20 empty] | 0.1W
8004 |  |  |  |  | Vpv10 | [7 empty] | PV10 voltage | [20 empty] | 0.1V
8005 |  |  |  |  | PV10Curr | [7 empty] | PV10 input current | [20 empty] | 0.1A
8006 |  |  |  |  | Ppv10 H | [7 empty] | PV10 input power(high) | [20 empty] | 0.1W
8007 |  |  |  |  | Ppv10 L | [7 empty] | PV10 input power(low) | [20 empty] | 0.1W
8008 |  |  |  |  | Epv9_today H | [7 empty] | PV9Energy today(high) | [20 empty] | 0.1kWh
8009 |  |  |  |  | Epv9_today L | [7 empty] | PV9Energy today (low) | [20 empty] | 0.1kWh
8010 |  |  |  |  | Epv9_total H | [7 empty] | PV9Energy total(high) | [20 empty] | 0.1kWh
8011 |  |  |  |  | Epv9_total L | [7 empty] | PV9Energy total (low) | [20 empty] | 0.1kWh
8012 |  |  |  |  | Epv10_today H | [7 empty] | PV10Energy today(high) | [20 empty] | 0.1kWh
8013 |  |  |  |  | Epv10_today L | [7 empty] | PV10Energy today (low) | [20 empty] | 0.1kWh
8014 |  |  |  |  | Epv10_total H | [7 empty] | PV10Energy total(high) | [20 empty] | 0.1kWh
8015 |  |  |  |  | Epv10_total L | [7 empty] | PV10Energy total (low) | [20 empty] | 0.1kWh
8016 |  |  |  |  | V _String17 | [7 empty] | PV String17voltage | [20 empty] | 0.1V
8017 |  |  |  |  | Curr _String17 | [7 empty] | PV String17 current | [13 empty] | -15~15A | [6 empty] | 0.1A
8015 |  |  |  |  | V _String18 | [7 empty] | PV String18voltage | [20 empty] | 0.1V
8016 |  |  |  |  | Curr _String18 | [7 empty] | PV String18current | [13 empty] | -15~15A | [6 empty] | 0.1A
8017 |  |  |  |  | V _String19 | [7 empty] | PV String19voltage | [20 empty] | 0.1V
8018 |  |  |  |  | Curr _String19 | [7 empty] | PV String19current | [13 empty] | -15~15A | [6 empty] | 0.1A
8019 |  |  |  |  | V _String20 | [7 empty] | PV String20voltage | [20 empty] | 0.1V
8020 |  |  |  |  | Curr _String20 | [7 empty] | PV String20current | [13 empty] | -15~15A | [6 empty] | 0.1A
8021 |  |  |  |  | PID PV9+ Voltage | [7 empty] | PID PV9PE voltage | [13 empty] | 0~1000V | [6 empty] | 0.1V
8022 |  |  |  |  | PID PV9+ Current | [7 empty] | PID PV9PE current | [13 empty] | -10~10mA | [6 empty] | 0.1mA
8023 |  |  |  |  | PID PV10+ Voltage | [7 empty] | PID PV10PE voltage | [13 empty] | 0~1000V | [6 empty] | 0.1V
8024 |  |  |  |  | PID PV10+ Current | [7 empty] | PID PV10PE current | [13 empty] | -10~10mA | [6 empty] | 0.1mA
8028 |  |  |  |  | StrUnmatch2 | [7 empty] | Bit0~15: String 17~32 unmatch
8029 |  |  |  |  | StrCurrentUnblan ce2 | [7 empty] | Bit0~15: String17~32 current unblance
8030 |  |  |  |  | StrDisconnect2 | [7 empty] | Bit0~15: String17~32 disconnect
8031 |  |  |  |  | PV Warning Value | [7 empty] | PV Warning Value (PV9-PV16) Contains PV9~16 abnormal , Boost9~16 Drive anomalies
8032 |  |  |  |  | StrWaringvalue1 | [7 empty] | string1~string16 abnormal
8033 |  |  |  |  | StrWaringvalue2 | [7 empty] | string17~string32 abnormal
8034 |  |  |  |  | BAT_Volt | [7 empty] | Battery voltage | [20 empty] | 0.1V
8035 |  |  |  |  | BAT_Curr | [7 empty] | Battery current | [20 empty] | 0.1A
8036 |  |  |  |  | STS_R_Volt_Rms | [7 empty] | STSphase R grid voltage | [20 empty] | 0.1V
8037 |  |  |  |  | STS_S_Volt_Rms | [7 empty] | STSphase S grid voltage | [20 empty] | 0.1V
8038 |  |  |  |  | STS_T_Volt_Rms | [7 empty] | STSphase T grid voltage | [20 empty] | 0.1V
8039 |  |  |  |  | STS_RS_Volt_Rms | [7 empty] | STS Line RS voltage | [20 empty] | 0.1V
8040 |  |  |  |  | STS_ST_Volt_Rms | [7 empty] | STS Line ST voltage | [20 empty] | 0.1V
8041 |  |  |  |  | STS_TR_Volt_Rms | [7 empty] | STS Line TR voltage | [20 empty] | 0.1V
8042 |  |  |  |  | STS_R _LOAD_CURR_Rm s | [7 empty] | STS phaseR Load Current | [20 empty] | 0.1A
8043 |  |  |  |  | STS_S _LOAD_CURR_Rm s | [7 empty] | STS phaseS Load Current | [20 empty] | 0.1A
8044 |  |  |  |  | STS_T _LOAD_CURR_Rm s | [7 empty] | STSphase T Load Current | [20 empty] | 0.1A
8045 |  |  |  |  | Pself H | [7 empty] | self-use power | [20 empty] | 0.1W
8046 |  |  |  |  | Pself L
8047 |  |  |  |  | Esys_today H | [7 empty] | System energy today | [20 empty] | 0.1kwh
8048 |  |  |  |  | Esys_today L
8049 |  |  |  |  | Edischr_today H | [7 empty] | Today discharge energy | [20 empty] | 0.1kWh
8050 |  |  |  |  | Edischr_today L
8051 |  |  |  |  | Edischr_total H | [7 empty] | Total discharge energy | [20 empty] | 0.1kWh
8052 |  |  |  |  | Edischr_total L
8053 |  |  |  |  | Echr_today H | [7 empty] | Charge energy today | [20 empty] | 0.1kWh
8054 |  |  |  |  | Echr_today L
8055 |  |  |  |  | Echr_total H | [7 empty] | Charge energy total | [20 empty] | 0.1kWh
8056 |  |  |  |  | Echr_total L
8057 |  |  |  |  | Eacchr_today H | [7 empty] | Today energy of AC charge | [20 empty] | 0.1kWh
8058 |  |  |  |  | Eacchr_today L
8059 |  |  |  |  | Eacchr_total H | [7 empty] | Total energy of AC charge | [20 empty] | 0.1kWh
8060 |  |  |  |  | Eacchr_total L
8061 |  |  |  |  | Esys_total H | [7 empty] | Total energy of system output | [20 empty] | 0.1kWh
8062 |  |  |  |  | Esys_total L
8063 |  |  |  |  | Eself_today H | [7 empty] | Today energy of Self output | [20 empty] | 0.1kWh
8064 |  |  |  |  | Eself_today L
8065 |  |  |  |  | Eself_total H | [7 empty] | Total energy of Self output | [20 empty] | 0.1kwh
8066 |  |  |  |  | Eself_ total L
8067 |  |  |  |  | Etouser_today H | [7 empty] | Today energy to user | [20 empty] | 0.1kWh
8068 |  |  |  |  | Etouser_today L
8069 |  |  |  |  | Etouser_total H | [7 empty] | Total energy to user | [20 empty] | 0.1kWh
8070 |  |  |  |  | Etouser_total L
8071 |  |  |  |  | Etogrid_today H | [7 empty] | Today energy to grid | [20 empty] | 0.1kWh
8072 |  |  |  |  | Etogrid_today L
8073 |  |  |  |  | Etogrid_total H | [7 empty] | Total energy to grid | [20 empty] | 0.1kWh
8074 |  |  |  |  | Etogrid_total L
8075 |  |  |  |  | Eload_today H | [7 empty] | Today energy of user load | [20 empty] | 0.1kWh
8076 |  |  |  |  | Eload_today L
8077 |  |  |  |  | Eload_total H | [7 empty] | Total energy of user load | [20 empty] | 0.1kWh
8078 |  |  |  |  | Eload_total L
8079 |  |  |  |  | Ptoload total H | [7 empty] | Total load power | [20 empty] | 0.1W
8080 |  |  |  |  | Ptoload total L
8081 |  |  |  |  | Ptouser total H | [7 empty] | Total forward power | [20 empty] | 0.1W
8082 |  |  |  |  | Ptouser total L
8083 |  |  |  |  | Ptogrid total H | [7 empty] | Total reverse power | [20 empty] | 0.1W
8084 |  |  |  |  | Ptogrid total L
8085 |  |  |  |  | Psys H | [7 empty] | System output power | [20 empty] | 0.1W
8086 |  |  |  |  | Psys L
8087 |  |  |  |  | usingtime_busca p_H | [7 empty] | Bus capacitor use time | [20 empty] | 1H
8088 |  |  |  |  | usingtime_busca p_L
8089 |  |  |  |  | running_Time_H | [7 empty] | Run time | [20 empty] | 1H
8090 |  |  |  |  | running_Time_L
8091 |  |  |  |  | BatPower_H | [7 empty] | Battery power | [20 empty] | 0.1W
8092 |  |  |  |  | BatPower_L
8093 |  |  |  |  | SOC | [7 empty] | Battery SOC | [20 empty] | %
8094 |  |  |  |  | SOH | [7 empty] | Battery SOH | [20 empty] | %
8095 |  |  |  |  | BMS_BATVol | [7 empty] | BMS Batteryvoltage | [20 empty] | 0.1V
8096 |  |  |  |  | INV_R_Volt_Rms | [7 empty] | INV Phase R voltage | [20 empty] | 0.1V
8097 |  |  |  |  | INV_S_Volt_Rms | [7 empty] | INV Phase S voltage | [20 empty] | 0.1V
8098 |  |  |  |  | INV_T_Volt_Rms | [7 empty] | INV Phase T voltage | [20 empty] | 0.1V
8099 |  |  |  |  | AC_CT_R_RMS | [7 empty] | AC Phase R Current | [20 empty] | 0.1A
8100 |  |  |  |  | AC_CT_S_RMS | [7 empty] | AC Phase S Current | [20 empty] | 0.1A
8101 |  |  |  |  | AC_CT_T_RMS | [7 empty] | AC Phase T Current | [20 empty] | 0.1A
8102 |  |  |  |  | ExtraAC Power to grid_H | [7 empty] | Extra invert power H | [20 empty] | 0.1kW
8103 |  |  |  |  | ExtraAC Power to grid_L | [7 empty] | Extra invert power L | [20 empty] | 0.1kWh
8104 |  |  |  |  | Eextra_today H | [7 empty] | Today energy of Extra invert(H) | [20 empty] | 0.1kWh
8105 |  |  |  |  | Eextra_today L | [7 empty] | Today energy of Extra invert (L) | [20 empty] | 0.1kWh
8106 |  |  |  |  | Eextra_total H | [7 empty] | Total energy of Extra invert (H) | [20 empty] | 0.1kWh
8107 |  |  |  |  | Eextra_total L | [7 empty] | Total energy of Extra invert (L) | [20 empty] | 0.1kWh
8108 |  |  |  |  | ATS SCR temperature | [28 empty] | 0.1C
8109 |  |  |  |  | ATS Relays temperature | [28 empty] | 0.1C
8110 |  |  |  |  | ATS interior temperature | [28 empty] | 0.1C
2.3 Meter register（Function code 0x20）
NO. |  |  |  |  | Variable Name | [6 empty] | Description | [17 empty] | Range | [5 empty] | Unit |  |  |  |  | Note
1 |  |  |  |  | Reserved
2 |  |  |  |  | Reserved
3 |  |  |  |  | Reserved
4 |  |  |  |  | Reserved
5 |  |  |  |  | Reserved
6 |  |  |  |  | Reserved
7 |  |  |  |  | Reserved
8 |  |  |  |  | L1 Current | [6 empty] | L1 phase current | [23 empty] | 0.1A
9
10 |  |  |  |  | L2 Current | [6 empty] | L2 phase current | [23 empty] | 0.1A
11
12 |  |  |  |  | Reserved
13 |  |  |  |  | Reserved
14 |  |  |  |  | L1ActivePow | [6 empty] | L1 phase active power | [23 empty] | 0.1W
15 |  |  |  |  | er
16 |  |  |  |  | L2ActivePow er | [6 empty] | L2 phase active power | [23 empty] | 0.1W
17
18-37 |  |  |  |  | Reserved
38 |  |  |  |  | TotalActiveP ower | [6 empty] | Total active power | [23 empty] | 0.1W
39
3 Set address Refer to the Inverter user manual. Always is : Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.
4 Notice 1) It can drive mostly 32 pv inverters for one RS485 comport. 2) There are only read input and hold registers commands even the newest version. 3) App user could only care the input register. 4) App user could not care the holding registers. 5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers.
5 Attachment
5.1 Data format
Address | [6 empty] | Function | [11 empty] | Data | [12 empty] | CRC Check
8 bits | [6 empty] | 8 bits | [11 empty] | N×8 bits | [12 empty] | 16 bits
The valid slave address range is 0 - 254 decimal. The address range assigned to each slave device is 1-254. 0 is a broadcast address. Each hold and input register is a 16 bit (two bytes) unsigned integer.
5.2 Command format (1）Function code 0x03 read hold register
Send Message:
Field Name | [18 empty] | Example(HEX)
Slave Address | [18 empty] | 11
Function | [18 empty] | 3
Starting Address Hi | [18 empty] | 0
Starting Address Lo | [18 empty] | 6B
No. of Points Hi | [18 empty] | 0
No. of Points Lo | [18 empty] | 3
Error Check(LRC or CRC) | [18 empty] | -
Response Message:
Field Name | [34 empty] | Example(HEX)
Slave Address | [34 empty] | 11
Function | [34 empty] | 3
Byte Count | [34 empty] | 6
Data Hi | [34 empty] | 2
Data Lo | [34 empty] | 2B
Data Hi | [34 empty] | 0
Data Lo | [34 empty] | 0
Data Hi | [34 empty] | 0
Data Lo | [34 empty] | 64
Error Check(LRC or CRC) | [34 empty] | -
Response error:11 0x80 ¦ 0x03 Errornum ber CRC (Errornum is a byte)
(2) Function code 0x04 read input register Send Message:
Field Name | [34 empty] | Example(HEX)
Slave Address | [34 empty] | 11
Function | [34 empty] | 4
Starting Address Hi | [34 empty] | 0
Starting Address Lo | [34 empty] | 8
No. of Points Hi | [34 empty] | 0
No. of Points Lo | [34 empty] | 1
Error Check(LRC or CRC) | [19 empty] | -
Response Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 4
Byte Count | [19 empty] | 2
Data Hi | [19 empty] | 0
Data Lo | [19 empty] | 0A
Error Check(LRC or CRC) | [19 empty] | -
Response error:11 0x80 ¦ 0x04 Errornum CRC (Errornum is a byte)
(3) Function code 0x06 preset single register Send Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 6
Register Address Hi | [19 empty] | 0
Register Address Lo | [19 empty] | 1
Preset Data Hi | [19 empty] | 0
Preset Data Lo | [19 empty] | 3
Error Check(LRC or CRC) | [19 empty] | -
Response Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 6
Register Address Hi | [19 empty] | 0
Register Address Lo | [19 empty] | 1
Preset Data Hi | [19 empty] | 0
Preset Data Lo | [19 empty] | 3
Error Check(LRC or CRC) | [19 empty] | -
Response error:11 0x80¦0x06 Errornum CRC (Errornum is a byte)
(4) Function code 0x10: preset multiple registers Send Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 10
Starting Address Hi | [19 empty] | 0
Starting Address Lo | [19 empty] | 1
No. of Registers Hi | [19 empty] | 0
No. of Registers Lo | [19 empty] | 2
Byte Count | [19 empty] | 4
Data Hi | [19 empty] | 0
Data Lo | [19 empty] | 0A
Data Hi | [19 empty] | 1
Data Lo | [19 empty] | 2
Error Check(LRC or CRC) | [19 empty] | -
Response Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 10
Starting Address Hi | [19 empty] | 0
Starting Address Lo | [19 empty] | 1
No. of Registers Hi | [19 empty] | 0
No. of Registers Lo | [19 empty] | 2
Error Check(LRC or CRC) | [19 empty] | -
Response Error:11 0x80¦0x10 Errornum CRC (Errornum is a byte) (5）Function code 0x20 read hold register
Send Message:
| Field Name | [18 empty] | Example(HEX)
| Slave Address | [18 empty] | 11
| Function | [18 empty] | 20
| Starting Address Hi | [18 empty] | 0
| Starting Address Lo | [18 empty] | 6B
| No. of Points Hi | [18 empty] | 0
No. of Points Lo | [19 empty] | 3
Error Check(LRC or CRC) | [19 empty] | -
Response Message:
Field Name | [19 empty] | Example(HEX)
Slave Address | [19 empty] | 11
Function | [19 empty] | 20
Byte Count | [19 empty] | 6
Data Hi | [19 empty] | 2
Data Lo | [19 empty] | 2B
Data Hi | [19 empty] | 0
Data Lo | [19 empty] | 0
Data Hi | [19 empty] | 0
Data Lo | [19 empty] | 64
Error Check(LRC or CRC) | [19 empty] | -
Response error:11 0x80 ¦ 0x20 Errornum ber CRC (Errornum is a byte)
Error codes:
| Description | [12 empty] | Code | [12 empty] | Meaning
| Illegal function | [12 empty] | 0x01 | [12 empty] | 1 write undefined function code 2 write reading only registers 3 read writing only registers
| Illegal data address | [12 empty] | 0x02 | [12 empty] | 1 write undefined address 2 read undefined address 3 read data crossing multi-groups
Illegal data | [12 empty] | 0x03 | [13 empty] | 1 write data over prescribed scope
Checkout fault | [12 empty] | 0x08 | [13 empty] | 1 CRC checkout error
5.3 Device Message Transmission Mode / Framing 5.3.1 RTU Mode When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream. The format for each byte in RTU mode is: Coding System: 8–bit binary, hexadecimal 0–9, A–F Two hexadecimal characters contained in each 8–bit field of the message Bits per Byte: 1 start bit 8 data bits, least significant bit sent first None parity 1 stop bit Error Check Field: Cyclical Redundancy Check (CRC) The baud rate of the transmission is:Default Baud Rate: 9600 bps,which can be set through hold register 22. Minimum CMD period (RS485 Time out): 850ms.Wait for minimum 850ms to send a new CMD after last CMD. Suggestion is 1s. 5.3.2 Maximum Data Length Definition Maximum read data length is 125 words in read command;Maximum update data length is 125 words in preset command. Note: Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers.
6 Appendix table Table 1: Inverter derating mode (Input 3086)
Derating Explanation Derating Logic Mode
0 No derating NA Derating starts when Bus>500V, reduction of 1%Pn for every
|  | 1 Bus voltage high derating 2 Aging fixed power derating 3 Grid voltage high derating 4 Over-frequency reduce derating | [17 empty] | 1V. During the test before aging,the load is limited to 30% Pn 60% Pn and 80% Pn respectively. When the grid voltage is >1.06Vn, the output is reduced based on the rated power. When the grid frequency is higher then over-frequency decrease point, output reduce 33.33%Pn/Hz.
5 Single DC source mode derating Single DC source Boost off, output limited to 3600W.
Inverter module over-temperature 6 derating User activated setting to limit 7 output derating 8 Load speed process derating 9 Over back by time derating Internal environment over- 10 temperature derating External environment 11 over-temperature derating | [20 empty] | When the module temperature is >109℃, the power decreases by 20%Pn every 1℃ it rises. Temperature >75℃, for every 1℃ rise, power drops by 20%Pn.
12 Wire impedance derating Parallel inverter export limit
13 derating
14 Single inverter export limit derating 15 Load first mode derating 16 CT installation issue derating | [21 empty] | When the meter or CT is turned on, it will take effect when the grid connection is successfully detected and the wrong or reversed connection is detected.
17 Zero current mode derating IEEE1547 grid voltage <0.5Vn or >1.1Vn, output limited to 0. Boost module over-temperature
|  | 18 derating | [5 empty] | Temperature>105 ℃, load derating 0.1%Pn every 200ms.
19 Zero power mode derating 20 Under-frequency increase derating 21 Bus bar current limit derating | [20 empty] | When the grid frequency is lower then under-frequency increase point,output increase 33.33%Pn/Hz.
Table 2: Battery derating mode (Input 3165)
Derating Mode | [18 empty] | Explanation
0 | [18 empty] | Normal, unrestricted
1 | [18 empty] | System fault
2 | [18 empty] | System warning
3 | [18 empty] | Maximum charging current of battery (charging)
4 | [18 empty] | Battery high temperature (charging)
5 | [18 empty] | Reserve (charging)
6 | [18 empty] | SOC setting limits (charging)
7 | [18 empty] | Battery low temperature (charging)
8 | [18 empty] | High bus voltage (charging)
9 | [18 empty] | Full charged(charging)
10 | [18 empty] | Reserve (charging)
11 | [18 empty] | System warning no charging (charging)
12 | [18 empty] | User setting the current of charging(charging)
13 | [18 empty] | BM charge current limited (charging)
14 | [18 empty] | Reserve (charging)
15 | [18 empty] | Reserve (charging)
16 | [18 empty] | Reserve (charging)
17 | [18 empty] | Maximum battery current limit (discharge)
18 | [18 empty] | Battery discharge Enable (discharge)
19 | [18 empty] | High bus discharge derating (discharge)
20 | [18 empty] | High temperature discharge derating (discharge)
21 | [18 empty] | System warning no discharge (discharge)
22 | [18 empty] | User setting the current of discharging(discharge)
23 | [18 empty] | BM discharge current limited (discharge)
24 | [18 empty] | Reserved (discharge)
25 | [18 empty] | Reserved (discharge)
26 | [18 empty] | Reserved (discharge)
27 | [18 empty] | Reserved (discharge)
28 | [18 empty] | Reserved (discharge)
29 | [18 empty] | Reserved (discharge)
30 | [18 empty] | Reserved (discharge)
31 | [18 empty] | Reserved (discharge)
32 | [18 empty] | Reserved (discharge)