## Table 1
Growatt Inverter Modbus RTU Protocol V1.24 Make： weiwei.shi Check： qixing.ren Authorize： liangcai.wu Effective date：
Change Record
Index |  |  |  | Version | [5 empty] | Change Content | [15 empty] | Make | [5 empty] | Make date
1 |  |  |  | 0 | [5 empty] | First Republic | [15 empty] | Weiwei.shi | [5 empty] | 2020-04-28
Instruction：Register range for various types of inverter TL-X/TL-XH/TL-XH US（MIN Type）：03 register range：0~124,3000~3124， 3125~3249(TL-XHUS) ； 04 register range ： 3000~3124,3125~3249 ， 3250~3374（TL-XH） TL3-X(MAX、MID、MAC Type)：03 register range：0~124,125~249； 04 register range：0~124,125~249 MAX 1500V、MAX-X LV: 03 register range：0~124,125~249；04 register range：0~124,125~249,875~999 MOD TL3-XH: 03 register range：0~124,3000~3124；04 register range： 3000~3124,3125~3249 Storage(MIX Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124 Storage(SPA Type)：03 register range：0~124,1000~1124；04 register range：1000~1124,2000~2124，1125~1249 Storage(SPH Type)：03 register range：0~124,1000~1124；04 register range：0~124,1000~1124，1125~1249
catalog 1 Data format 5 2 Command Format 5 3 Device Message Transmission Mode / Framing 8 4 Register map 9 4.1 Holding Reg 9 4.2 Input Reg 47 5 Set address 84 6 Notice 84
1 Data format
Valid slave device addresses are in the range of 0 – 254 decimal. The individual slave devices are assigned addresses in the range of 1 – 254. 0 is the broadcast address It is 16bits (two bytes) unsigned integer for each holding and input register; 2 Command Format Function 3 Read holding register
Response Error: 11 0x80¦0x03 ErrornumCRC(Errornum as a byte) Function 4 Read input register Response Error: 11 0x80¦0x04 ErrornumCRC (Errornum as a byte) Function 6 Preset single register
Response Error: 11 0x80¦0x06 ErrornumCRC (Errornum as a byte) Function 16 Preset multiple register Response Error: 11 0x80¦0x10 ErrornumCRC (Errornum as a byte)
3 Device Message Transmission Mode / Framing RTU Mode When controllers are setup to communicate on a Modbus network using RTU (Remote Terminal Unit) mode, each 8–bit byte in a message contains two 4–bit hexadecimal characters. Each message must be transmitted in a continuous stream. The format for each byte in RTU mode is: Coding System: 8–bit binary, hexadecimal 0–9, A–F Two hexadecimal characters contained in each 8–bit field of the message
Bits per Byte: |  |  |  |  | 1 start bit 8 data bits, least significant bit sent first None parity 1 stop bit Error Check Field: Cyclical Redundancy Check (CRC)
The baud rate of the transmission is: Default Baud Rate: 9600 bps Can be set through hold register 22 Minimum CMD period (RS485 Time out): 850ms. Wait for minimum850ms to send a new CMD after last CMD. Suggestion is 1s; Maximum Data Length Define: Maximum read data length is 125 words in read command; Maximum update data length is 125 words in preset command; Note: Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing other registers;
4 Register map It is 16bits (two bytes) unsigned integer for each holding and input register; 4.1 Holding Reg
Registe r NO. |  |  | Variable Name | [5 empty] | Description | [6 empty] | Write or not |  |  | Value |  |  | Unit |  |  |  | Initial value | Note
First group
0 |  |  | OnOff | [5 empty] | Remote On/Off . On（1）；Of（f 0）Inverter On（3）；Off（2）BDC | [6 empty] | W |  |  | 0、1、2、 3 | [6 empty] | 1 | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function.
1 |  |  | SaftyFuncEn | [5 empty] | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable | [6 empty] | W |  |  | 0 : disable 1: enable | [7 empty] | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA
Bit10：Split phase enable
Bit10~15:预留
2 |  |  | PF CMD memory state | [5 empty] | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. | [6 empty] | W |  |  | 0or1 | [6 empty] | 0 | Means these settings will be acting or not when next power on
3 |  |  | Active P Rate | [5 empty] | Inverter Max output active power percent | [6 empty] | W |  |  | 0-100 or 255 |  |  | % |  |  |  | 255 | 255: power is not be limited
4 |  |  | Reactive P Rate | [5 empty] | Inverter max output reactive power percent | [6 empty] | W |  |  | -100-100 or 255 |  |  | % |  |  |  | 255 | 255: power is not be limited
5 |  |  | Power factor | [5 empty] | Inverter output power factor’s 10000 times | [6 empty] | W |  |  | 0-20000, 0-10000 is underexci ted, other is overexcit ed | [6 empty] | 0
6 |  |  | Pmax H | [5 empty] | Normal power (high) | [12 empty] | 0.1VA
7 |  |  | Pmax L | [5 empty] | Normal power (low) | [12 empty] | 0.1VA
8 |  |  | Vnormal | [5 empty] | Normal work PV voltage | [12 empty] | 0.1V
9 |  |  | Fw version H | [5 empty] | Firmware version (high) | [12 empty] | ASCII
10 |  |  | Fw version M | [5 empty] | Firmware version (middle)
11 |  |  | Fw version L | [5 empty] | Firmware version (low)
12 |  |  | Fw version2 H | [5 empty] | Control Firmware version (high) | [12 empty] | ASCII
13 |  |  | Fw version2 M | [5 empty] | Control Firmware version (middle)
14 |  |  | Fw version2 L | [5 empty] | Control Firmware version (low)
15 |  |  | LCD language | [5 empty] | LCD language | [6 empty] | W |  |  | 0-5 | [7 empty] | 0: Italian; 1: English; 2: German; 3: Spanish; 4: French; 5: Chinese; 6：Polish 7：Portugues 8：Hungary
16 |  |  | CountrySele cted | [5 empty] | Country Selected or not | [6 empty] | W |  |  | 0: need to select; 1: have selected
17 |  |  | Vpv start | [5 empty] | Input start voltage | [6 empty] | W | [5 empty] | 0.1V
18 |  |  | Time start | [5 empty] | Start time | [6 empty] | W | [5 empty] | 1s
19 |  |  | RestartDelay Time | [5 empty] | Restart Delay Time after fault back; | [6 empty] | W | [5 empty] | 1s
20 |  |  | wPowerStart Slope | [5 empty] | Power start slope | [6 empty] | W |  |  | 1-1000 |  |  | 0.1%
21 |  |  | wPowerRest artSlopeEE | [5 empty] | Power restart slope | [6 empty] | W |  |  | 1-1000 |  |  | 0.1%
22 |  |  | wSelectBaud rate | [5 empty] | Select communicationbaudrat e 0: 9600bps 1:38400bps | [6 empty] | W |  |  | 0-1 | [6 empty] | 0
23 |  |  | Serial NO | [5 empty] | Serial number 1-2 | [12 empty] | ASCII
24 |  |  | Serial NO | [5 empty] | Serial number 3-4
25 |  |  | Serial NO | [5 empty] | Serial number 5-6
26 |  |  | Serial NO | [5 empty] | Serial number 7-8
27 |  |  | Serial NO | [5 empty] | Serial number 9-10
28 |  |  | Module H | [5 empty] | Inverter Module (high) | [9 empty] | &*5
29 |  |  | Module L | [5 empty] | Inverter Module (low) | [9 empty] | &*5
30 |  |  | Com Address | [5 empty] | Communicate address | [6 empty] | W |  |  | 1-254 | [6 empty] | 1
31 |  |  | FlashStart | [5 empty] | Update firmware | [6 empty] | W |  |  | 1
32 |  |  | Reset User Info | [5 empty] | Reset User Information | [6 empty] | W |  |  | 0x0001
33 |  |  | Reset to factory | [5 empty] | Reset to factory | [6 empty] | W |  |  | 0x0001
34 |  |  | Manufacture r Info 8 | [5 empty] | Manufacturer information (high) | [12 empty] | ASCII
35 |  |  | Manufacture r Info 7 | [5 empty] | Manufacturer information (middle)
36 |  |  | Manufacture r Info 6 | [5 empty] | Manufacturer information (low)
37 |  |  | Manufacture r Info 5 | [5 empty] | Manufacturer information (high)
38 |  |  | Manufacture r Info 4 | [5 empty] | Manufacturer information (middle)
39 |  |  | Manufacture r Info3 | [5 empty] | Manufacturer information (low)
40 |  |  | Manufacture r Info 2 | [5 empty] | Manufacturer information (low)
41 |  |  | Manufacture r Info 1 | [5 empty] | Manufacturer information (high)
42 |  |  | bfailsafeEn; | [5 empty] | G100 fail safe | [6 empty] | W |  |  | Enable:1 Disable:0 | [7 empty] | English G100 fail safe set
43 |  |  | DTC | [5 empty] | Device Type Code | [9 empty] | &*6
44 |  |  | TP | [5 empty] | Input tracker num and output phase num | [9 empty] | Eg:0x020 3 is two MPPT and 3ph output
45 |  |  | Sys Year | [5 empty] | System time-year | [6 empty] | W |  |  | Year offset is 0 | [7 empty] | Local time
46 |  |  | Sys Month | [5 empty] | System time- Month | [6 empty] | W
47 |  |  | Sys Day | [5 empty] | System time- Day | [6 empty] | W
48 |  |  | Sys Hour | [5 empty] | System time- Hour | [6 empty] | W
49 |  |  | Sys Min | [5 empty] | System time- Min | [6 empty] | W
50 |  |  | Sys Sec | [5 empty] | System time- Second | [6 empty] | W
51 |  |  | Sys Weekly | [5 empty] | System Weekly | [6 empty] | W |  |  | 0-6
52 |  |  | Vac low | [5 empty] | Grid voltage low limit protect | [6 empty] | W | [5 empty] | 0.1V
53 |  |  | Vac high | [5 empty] | Grid voltage high limit protect | [6 empty] | W | [5 empty] | 0.1V
54 |  |  | Fac low | [5 empty] | Grid frequency low limit protect | [6 empty] | W | [5 empty] | 0.01 Hz
55 |  |  | Fac high | [5 empty] | Grid high frequencylimit protect | [6 empty] | W | [5 empty] | 0.01 Hz
56 |  |  | Vac low 2 | [5 empty] | Grid voltage low limit protect 2 | [6 empty] | W | [5 empty] | 0.1V
57 |  |  | Vac high 2 | [5 empty] | Grid voltage high limit protect 2 | [6 empty] | W | [5 empty] | 0.1V
58 |  |  | Fac low 2 | [5 empty] | Grid frequency low limit protect 2 | [6 empty] | W | [5 empty] | 0.01 Hz
59 |  |  | Fac high 2 | [5 empty] | Grid high frequency limit protect 2 | [6 empty] | W | [5 empty] | 0.01 Hz
60 |  |  | Vac low 3 | [5 empty] | Grid voltage low limit protect 3 | [6 empty] | W | [5 empty] | 0.1V
61 |  |  | Vac high 3 | [5 empty] | Grid voltage high limit protect 3 | [6 empty] | W | [5 empty] | 0.1V
62 |  |  | Fac low 3 | [5 empty] | Grid frequency low limit protect 3 | [6 empty] | W | [5 empty] | 0.01Hz
63 |  |  | Fac high 3 | [5 empty] | Grid frequency high limit protect 3 | [6 empty] | W | [5 empty] | 0.01Hz
64 |  |  | Vac low C | [5 empty] | Grid low voltage limit connect to Grid | [6 empty] | W | [5 empty] | 0.1V
65 |  |  | Vac high C | [5 empty] | Grid high voltage limit connect to Grid | [6 empty] | W | [5 empty] | 0.1V
66 |  |  | Fac low C | [5 empty] | Grid low frequency | [6 empty] | W | [5 empty] | 0.01
[9 empty] | limit connect to Grid | [12 empty] | Hz
67 |  |  | Fac high C | [5 empty] | Grid high frequency limit connect to Grid | [6 empty] | W | [5 empty] | 0.01 Hz
68 |  |  | Vac low1 time | [5 empty] | Grid voltage low limit protect time 1 | [6 empty] | W | [5 empty] | Cycle
69 |  |  | Vac high1 time | [5 empty] | Grid voltage high limit protect time 1 | [6 empty] | W | [5 empty] | Cycle
70 |  |  | Vac low2 time | [5 empty] | Grid voltage low limit protect time 2 | [6 empty] | W | [5 empty] | Cycle
71 |  |  | Vac high2 time | [5 empty] | Grid voltage high limit protect time 2 | [6 empty] | W | [5 empty] | Cycle
72 |  |  | Fac low1 time | [5 empty] | Grid frequency low limit protect time 1 | [6 empty] | W | [5 empty] | Cycle
73 |  |  | Fac high1 time | [5 empty] | Grid frequency high limit protect time 1 | [6 empty] | W | [5 empty] | Cycle
74 |  |  | Fac low2 time | [5 empty] | Grid frequency low limit protect time 2 | [6 empty] | W | [5 empty] | Cycle
75 |  |  | Fac high2 time | [5 empty] | Grid frequency high limit protect time 2 | [6 empty] | W | [5 empty] | Cycle
76 |  |  | Vac low3 time | [5 empty] | Grid voltage low limit protect time 3 | [6 empty] | W | [5 empty] | Cycle
77 |  |  | Vac high3 time | [5 empty] | Grid voltage high limit protect time 3 | [6 empty] | W | [5 empty] | Cycle
78 |  |  | Fac low3 time | [5 empty] | Grid frequency low limit protect time 3 | [6 empty] | W | [5 empty] | Cycle
79 |  |  | Fac high3 time | [5 empty] | Grid frequency high limit protect time 3 | [6 empty] | W | [5 empty] | Cycle
80 |  |  | U10min | [5 empty] | Volt protection for 10 min | [6 empty] | W | [5 empty] | 0.1V |  |  |  | 1.1Vn
81 |  |  | PV Voltage High Fault | [5 empty] | PV Voltage High Fault | [6 empty] | W | [5 empty] | 0.1V
82 |  |  | FW Build No. 5 | [5 empty] | Model letter version number (TJ) | [12 empty] | ASCII
83 |  |  | FW Build No. 4 | [5 empty] | Model letter version number (AA) | [12 empty] | ASCII
84 |  |  | FW Build No. 3 | [5 empty] | DSP1 FW Build No. | [12 empty] | ASCII
85 |  |  | FW Build No. 2 | [5 empty] | DSP2/M0 FW Build No. | [12 empty] | ASCII
86 |  |  | FW Build No. 1 | [5 empty] | CPLD/AFCI FW Build No. | [12 empty] | ASCII
87 |  |  | FW Build No. | [5 empty] | M3 FW Build No. | [12 empty] | ASCII
0
88 |  |  | ModbusVers ion | [5 empty] | Modbus Version | [9 empty] | Eg：207 is V2.07 |  |  | Int(16 bits)
89 |  |  | PFModel | [5 empty] | Set PF function Model 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6：Q(v)model 7：Direct Control mode | [6 empty] | W
8. Static capacitive QV mode 9. Static inductive QV mode
90 |  |  | GPRS IP Flag | [5 empty] | Bit0-3:read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed Bit4-7:GPRS status | [6 empty] | W |  |  | Bit0-3:ab out GPRS IP SET Bit4-7:ab out GRPRS Status
91 |  |  | FreqDerateS tart | [5 empty] | Frequency derating start point | [6 empty] | W | [5 empty] | 0.01H Z
92 |  |  | FLrate | [5 empty] | Frequency – load limit rate | [6 empty] | W |  |  | 0-100 |  |  | 10tim es
93 |  |  | V1S | [5 empty] | CEI021 V1S Q(v) | [6 empty] | W |  |  | V1S<V2S |  |  | 0.1V
94 |  |  | V2S | [5 empty] | CEI021 V2S Q(v) | [6 empty] | W | [5 empty] | 0.1V
95 |  |  | V1L | [5 empty] | CEI021 V1L Q(v) | [6 empty] | W |  |  | V1L<V1S |  |  | 0.1V
96 |  |  | V2L | [5 empty] | CEI021 V2L Q(v) | [6 empty] | W |  |  | V2L<V1L |  |  | 0.1V
97 |  |  | Qlockinpow er | [5 empty] | Q(v) lock in active power of CEI021 | [6 empty] | W |  |  | 0-100 |  |  | Percen t
98 |  |  | QlockOutpo wer | [5 empty] | Q(v) lock Out active power of CEI021 | [6 empty] | W |  |  | 0-100 |  |  | Percen t
99 |  |  | LIGridV | [5 empty] | Lock in gird volt of CEI021 PF line | [6 empty] | W |  |  | nVn |  |  | 0.1V
100 |  |  | LOGridV | [5 empty] | Lock out gird volt of CEI021 PF line | [6 empty] | W |  |  | nVn |  |  | 0.1V
101 |  |  | PFAdj1 | [5 empty] | PF adjust value 1 | [9 empty] | 4096 is 1
102 |  |  | PFAdj2 | [5 empty] | PF adjust value 2 | [9 empty] | 4096 is 1
103 |  |  | PFAdj3 | [5 empty] | PF adjust value 3 | [9 empty] | 4096 is 1
104 |  |  | PFAdj4 | [5 empty] | PF adjust value 4 | [9 empty] | 4096 is 1
105 |  |  | PFAdj5 | [5 empty] | PF adjust value 5 | [9 empty] | 4096 is 1
106 |  |  | PFAdj6 | [5 empty] | PF adjust value 6 | [9 empty] | 4096 is 1
107 |  |  | QVRPDelayTi meEE | [5 empty] | QV Reactive Power delaytime | [6 empty] | W |  |  | 0-30 |  |  | 1S |  |  |  | 3S
108 |  |  | OverFDeratD elayTimeEE | [5 empty] | Overfrequency derati ngdelaytime | [6 empty] | W |  |  | 0-20 |  |  | 50ms |  |  |  | 0
109 |  |  | QpercentMa x | [5 empty] | Qmax for Q(V) curve | [6 empty] | W |  |  | 0-1000 |  |  | 0.1%
110 |  |  | PFLineP1_LP | [5 empty] | PF limit line point 1 load percent | [6 empty] | W |  |  | 0-255 |  |  | percen t |  |  |  |  | 255 means no this point
111 |  |  | PFLineP1_PF | [5 empty] | PF limit line point 1 power factor | [6 empty] | W |  |  | 0-20000
112 |  |  | PFLineP2_LP | [5 empty] | PF limit line point 2 load percent | [6 empty] | W |  |  | 0-255 |  |  | percen t |  |  |  |  | 255 means no this point
113 |  |  | PFLineP2_PF | [5 empty] | PF limit line point 2power factor | [6 empty] | W |  |  | 0-20000
114 |  |  | PFLineP3_LP | [5 empty] | PF limit line point 3 load percent | [6 empty] | W |  |  | 0-255 |  |  | percen t |  |  |  |  | 255 means no this point
115 |  |  | PFLineP3_PF | [5 empty] | PF limit line point 3 power factor | [6 empty] | W |  |  | 0-20000
116 |  |  | PFLineP4_LP | [5 empty] | PF limit line point 4 load percent | [6 empty] | W |  |  | 0-255 |  |  | percen t |  |  |  |  | 255 means no this point
117 |  |  | PFLineP4_PF | [5 empty] | PF limit line point 4 power factor | [6 empty] | W |  |  | 0-20000
118 |  |  | Module 4 | [5 empty] | Inverter Module (4) | [9 empty] | &*11 | [7 empty] | SxxBxx
119 |  |  | Module 3 | [5 empty] | Inverter Module (3) | [9 empty] | &*11 | [7 empty] | DxxTxx
120 |  |  | Module 2 | [5 empty] | Inverter Module (2) | [9 empty] | &*11 | [7 empty] | PxxUxx
121 |  |  | Module 1 | [5 empty] | Inverter Module (1) | [9 empty] | &*11 | [7 empty] | Mxxxx Power
122 |  |  | ExportLimit_ En/dis | [5 empty] | ExportLimit_En/dis | [6 empty] | R/W |  |  | 1/0 | [7 empty] | ExportLimit enable, 0: Disable exportLimit; 1: Enable 485 exportLimit; 2: Enable 232 exportLimit; 3: Enable CT exportLimit;
123 |  |  | ExportLimitP owerRate | [5 empty] | ExportLimitPowerRate | [6 empty] | R/W |  |  | -1000~+1 000 |  |  | 0.1% |  |  |  |  | ExportLimit PowerRate
124 |  |  | TrakerModel | [5 empty] | Traker Model | [6 empty] | W |  |  | 0,1,2 | [7 empty] | 0:Independent 1:DC Source 2:Parallel
Second group
125 |  |  | INV Type-1 | [5 empty] | Inverter type-1 | [6 empty] | R | [5 empty] | ASCII |  |  |  |  | Reserved
126 |  |  | INV Type-2 | [5 empty] | Inverter type-2 | [6 empty] | R | [5 empty] | ASCII
127 |  |  | INV Type-3 | [5 empty] | Inverter type-3 | [6 empty] | R | [5 empty] | ASCII
128 |  |  | INV Type-4 | [5 empty] | Inverter type-4 | [6 empty] | R | [5 empty] | ASCII
129 |  |  | INV Type-5 | [5 empty] | Inverter type-5 | [6 empty] | R | [5 empty] | ASCII
130 |  |  | INV Type-6 | [5 empty] | Inverter type-6 | [6 empty] | R | [5 empty] | ASCII
131 |  |  | INV Type-7 | [5 empty] | Inverter type-7 | [6 empty] | R | [5 empty] | ASCII
132 |  |  | INV Type-8 | [5 empty] | Inverter type-8 | [6 empty] | R | [5 empty] | ASCII
133 |  |  | BLVersion1 | [5 empty] | Boot loader version1 | [6 empty] | R | [10 empty] | Reserved
134 |  |  | BLVersion2 | [5 empty] | Boot loader version2 | [6 empty] | R | [10 empty] | Reserved
135 |  |  | BLVersion3 | [5 empty] | Boot loader version3 | [6 empty] | R | [10 empty] | Reserved
136 |  |  | BLVersion4 | [5 empty] | Boot loader version4 | [6 empty] | R | [10 empty] | Reserved
137 |  |  | Reactive P ValueH | [5 empty] | Reactive PowerH | [6 empty] | R/W | [5 empty] | 0.1var
138 |  |  | Reactive P ValueL | [5 empty] | Reactive PowerL | [6 empty] | R/W | [5 empty] | 0.1var
139 |  |  | ReactiveOut putPriorityE nable | [5 empty] | ReactiveOutput Priority Enable | [6 empty] | R/W | [5 empty] | 0/1 |  |  |  |  | 0：disable 1：enable
140 |  |  | Reactive P Value(Ratio) | [5 empty] | Reactive Power Ratio | [6 empty] | R/W | [5 empty] | 0.1
……
141 |  |  | SvgFunction Enable | [5 empty] | Svg enable on night | [6 empty] | R/W | [5 empty] | 0/1 |  |  |  |  | 0：disable 1：enable
142 |  |  | uwUnderFU ploadPoint | [5 empty] | UnderF Upload Point | [6 empty] | R/W | [5 empty] | 0.01H Z
143 |  |  | uwOFDerate RecoverPoin t | [5 empty] | OFDerate RecoverPoint | [6 empty] | R/W | [5 empty] | 0.01H Z
144 |  |  | uwOFDerate RecoverDela yTime | [5 empty] | OFDerate RecoverDelayTime | [6 empty] | R/W |  |  | 0-30000 |  |  | 50ms
145 |  |  | ZeroCurrent Enable | [5 empty] | ZeroCurrent Enable | [6 empty] | R/W |  |  | 0-1
146 |  |  | uwZeroCurre ntStaticlowV olt | [5 empty] | ZeroCurrent StaticlowVolt | [6 empty] | R/W |  |  | 46-230V |  |  | 0.1V |  |  |  | 115V
147 |  |  | uwZeroCurre ntStaticHigh Volt | [5 empty] | ZeroCurrent StaticHighVolt | [6 empty] | R/W |  |  | 230-276V |  |  | 0.1V |  |  |  | 276V
148 |  |  | uwHVoltDer | [5 empty] | HVoltDerate HighPoint | [6 empty] | R/W |  |  | 0-1000V |  |  | 0.1V
ateHighPoint
149 |  |  | uwHVoltDer ateLowPoint | [5 empty] | HVoltDerate LowPoint | [6 empty] | R/W |  |  | 0-1000V |  |  | 0.1V
150 |  |  | uwQVPower StableTime | [5 empty] | QVPower Stable Time | [6 empty] | R/W |  |  | 0-60S |  |  | 0.1S
151 |  |  | uwUnderFU ploadStopPo int | [5 empty] | UnderF Upload StopPoint | [6 empty] | R/W | [5 empty] | 0.01H Z
152 |  |  | fUnderFreqP oint | [5 empty] | Underfrequency load start point | [6 empty] | R/W |  |  | 46.00-50. 00 |  |  | 0.01Hz |  |  |  | 49.8 | CEI
153 |  |  | fUnderFreqE ndPoint | [5 empty] | Underfrequency down load end point | [6 empty] | R/W |  |  | 46.00-50. 00 |  |  | 0.01Hz |  |  |  | 49.1 | CEI
154 |  |  | fOverFreqPo int | [5 empty] | Over frequency loading start point | [6 empty] | R/W |  |  | 50.00-52. 00 |  |  | 0.01Hz |  |  |  | 50.2 | CEI
155 |  |  | fOverFreqEn dPoint | [5 empty] | Over frequency loading end point | [6 empty] | R/W |  |  | 50.00-52. 00 |  |  | 0.01Hz |  |  |  | 51.5 | CEI
156 |  |  | fUnderVoltP oint | [5 empty] | Undervoltage load shedding start point | [6 empty] | R/W |  |  | 160-300 |  |  | 0.1V |  |  |  | 220 | CEI
157 |  |  | fUnderVoltE ndPoint | [5 empty] | Undervoltage derating end point | [6 empty] | R/W |  |  | 160-300 |  |  | 0.1V |  |  |  | 207 | CEI
158 |  |  | fOverVoltPoi nt | [5 empty] | Overvoltage loading start point | [6 empty] | R/W |  |  | 160-300 |  |  | 0.1V |  |  |  | 230 | CEI
159 |  |  | fOverVoltEn dPoint | [5 empty] | Overvoltage loading end point | [6 empty] | R/W |  |  | 160-300 |  |  | 0.1V |  |  |  | 245 | CEI
160 |  |  | uwNominal GridVolt | [5 empty] | NominalGridVolt Select | [6 empty] | R/W |  |  | 0~3 | [7 empty] | UL
161 |  |  | uwGridWatt Delay | [5 empty] | GridWatt DelayTime | [6 empty] | R/W |  |  | 0~3000 |  |  | 20ms |  |  |  |  | UL
162 |  |  | uwReconnec tStartSlope | [5 empty] | Reconnect StartSlope | [6 empty] | R/W |  |  | 1~1000 |  |  | 0.1 |  |  |  |  | UL
163 |  |  | uwLFRTEE | [5 empty] | LFRT1 Freq | [6 empty] | R/W |  |  | 5500~650 0 |  |  | 0.01Hz |  |  |  |  | UL
164 |  |  | uwLFRTTime EE | [5 empty] | LFRT1 Time | [6 empty] | R/W | [5 empty] | 20ms |  |  |  |  | UL
165 |  |  | uwLFRT2EE | [5 empty] | LFRT2 Freq | [6 empty] | R/W |  |  | 5500~650 0 |  |  | 0.01Hz |  |  |  |  | UL
166 |  |  | uwLFRTTime 2EE | [5 empty] | LFRT2 Time | [6 empty] | R/W | [5 empty] | 20ms |  |  |  |  | UL
167 |  |  | uwHFRTEE | [5 empty] | HFRT1 Freq | [6 empty] | R/W |  |  | 5500~650 0 |  |  | 0.01Hz |  |  |  |  | UL
168 |  |  | uwHFRTTim eEE | [5 empty] | HFRT1 Time | [6 empty] | R/W | [5 empty] | 20ms |  |  |  |  | UL
169 |  |  | uwHFRT2EE | [5 empty] | HFRT2 Freq | [6 empty] | R/W |  |  | 5500~650 0 |  |  | 0.01Hz |  |  |  |  | UL
170 |  |  | uwHFRTTim e2EE | [5 empty] | HFRT2 Time | [6 empty] | R/W | [5 empty] | 20ms |  |  |  |  | UL
171 |  |  | uwHVRTEE | [5 empty] | HVRT1 Volt | [6 empty] | R/W | [5 empty] | 0.001 Un |  |  |  |  | UL
172 |  |  | uwHVRTTim eEE | [5 empty] | HVRT1 Time | [6 empty] | R/W | [5 empty] | 20ms |  |  |  |  | UL
173 |  |  | uwHVRT2EE | [5 empty] | HVRT2 Volt | [6 empty] | R/W | [5 empty] | 0.001 Un |  |  |  |  | UL
174 |  |  | uwHVRTTim e2EE | [5 empty] | HVRT2 Time | [6 empty] | R/W | [5 empty] | 0.001 Un |  |  |  |  | UL
175 |  |  | uwUnderFU ploadDelayTi me | [5 empty] | UnderF UploadDelayTime | [6 empty] | R/W |  |  | 0-2s |  |  | 50ms |  |  |  | 0s | 50549
176 |  |  | uwUnderFU ploadRateEE | [5 empty] | UnderF UploadRate | [6 empty] | R/W | [10 empty] | 50549
177 |  |  | uwGridResta rt_H_Freq | [5 empty] | GridRestart HighFreq | [6 empty] | R/W | [5 empty] | 0.01Hz |  |  |  |  | 50549
178 |  |  | OverFDeratR esponseTim e | [5 empty] | OverFDerat ResponseTime | [6 empty] | W/R |  |  | 0-500
179 |  |  | UnderFUplo adResponse Time | [5 empty] | UnderFUpload ResponseTime | [6 empty] | W/R |  |  | 0-500
Intelligent control reads relevant data, used to identify the logo 180-200
180 |  |  | MeterLink | [5 empty] | Whether to elect the meter | [6 empty] | R/W | [10 empty] | 0: Missed, 1: Received
181 |  |  | OPT Number | [5 empty] | Number of connection optimizers | [6 empty] | R/W |  |  | 0-64 | [7 empty] | The total number of optimizers connected to the inverter
182 |  |  | OPT ConfigOK Flag | [5 empty] | Optimizer configuration completion flag | [6 empty] | R/W | [10 empty] | 0x00:Not configured success 0x01:Configuration is complete
183 |  |  | PvStrScan | [5 empty] | String Num | [6 empty] | R/W |  |  | 0、8、16、 32 | [7 empty] | 0：Not support Other：PvString Num
184 |  |  | BDCLinkNum | [5 empty] | BDC parallel Num | [6 empty] | R/W | [10 empty] | The number of BDCs connected to the current machine Default is 0
185 |  |  | PackNum | [5 empty] | Number of battery modules | [6 empty] | R | [10 empty] | Total number of battery modules currently associated with all BDCs
186 |  |  | Reserved
187 |  |  | VPP function enable status | [5 empty] | VPP function enable status | [6 empty] | R | [10 empty] | 0：Disable 1：Enable
188 |  |  | dataLog Connect Server status | [5 empty] | dataLog Connect Server status | [17 empty] | 0：connection succeeded 1：Connection failed
……
200 |  |  | Reserved | [23 empty] | Reserved
201 |  |  | PID Working Model | [5 empty] | PID Operating mode | [6 empty] | W |  |  | 0: automati c 1: continuo us 2: All night
202 |  |  | PID On/Off Ctrl | [5 empty] | PID Break control | [6 empty] | W |  |  | 0:On 1:Off
203 |  |  | PID Volt Option | [5 empty] | PID Output voltage option | [6 empty] | W |  |  | 300~1000 |  |  | V
…… | [26 empty] | Reserved
209 |  |  | New Serial NO | [5 empty] | Serial number 1-2 | [12 empty] | ASCII
210 |  |  | New Serial NO | [5 empty] | Serial number 3-4 | [12 empty] | ASCII
211 |  |  | New Serial NO | [5 empty] | Serial number 5-6 | [12 empty] | ASCII
212 |  |  | New Serial NO | [5 empty] | Serial number 7-8 | [12 empty] | ASCII
213 |  |  | New Serial NO | [5 empty] | Serial number 9-10 | [12 empty] | ASCII
214 |  |  | New Serial NO | [5 empty] | Serial number 11-12 | [12 empty] | ASCII
215 |  |  | New Serial NO | [5 empty] | Serial number 13-14 | [12 empty] | ASCII
216 |  |  | New Serial |  |  | NO |  |  | Serial number 15-16 | [12 empty] | ASCII
217 |  |  | New Serial |  |  | NO |  |  | Serial number 17-18 | [12 empty] | ASCII
218 |  |  | New Serial |  |  | NO |  |  | Serial number 19-20 | [12 empty] | ASCII
219 |  |  | New Serial |  |  | NO |  |  | Serial number 21-22 | [12 empty] | ASCII
220 |  |  | New Serial |  |  | NO |  |  | Serial number 23-24 | [12 empty] | ASCII
221 |  |  | New Serial |  |  | NO |  |  | Serial number 25-26 | [12 empty] | ASCII
222 |  |  | New Serial |  |  | NO |  |  | Serial number 27-28 | [12 empty] | ASCII
223 |  |  | New Serial |  |  | NO |  |  | Serial number 29-30 | [12 empty] | ASCII
…… | [26 empty] | Reserved
229 |  |  | EnergyAdjus t | [5 empty] | Power generation incremental calibration coefficient | [6 empty] | W/R | [5 empty] | 0.1% |  |  |  |  | 1-1000,(Percent ratio)
230~249 for growatt debug setting
230 |  |  | IslandDisabl e | [5 empty] | Island Disable or not. 1:disable 0:Enable | [6 empty] | W |  |  | 0,1 | [6 empty] | 0
231 |  |  | FanCheck | [5 empty] | Start Fan Check | [6 empty] | W |  |  | 1
232 |  |  | EnableNLine | [5 empty] | Enable N Line of grid | [6 empty] | W |  |  | 1 | [6 empty] | 0
233 |  |  | wCheckHard ware | [5 empty] | wCheckHardware Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarni ng Bit9:EEWriteWarning ……
234 |  |  | wCheckHard ware2 | [23 empty] | reserved
235 |  |  | ubNToGNDD etect | [5 empty] | Dis/enable N to GND detect function | [6 empty] | W |  |  | 1:enable 0:disable | [6 empty] | 1
236 |  |  | NonStdVacE nable | [5 empty] | Enable/Disable Nonstandard Grid voltage range | [6 empty] | W |  |  | 0-2 | [6 empty] | 0 | 0:Disable; 1:Enable Voltgrade1 2:Enable Voltgrade2
237 |  |  | uwEnableSp ecSet | [5 empty] | Disablse/enable appointed spec setting | [6 empty] | W |  |  | 1:enable 0:disable |  |  | Binary |  |  |  | 0x000 0 | Bit 0: Hungary
238 |  |  | Fast MPPT enable | [5 empty] | About Fast mppt | [9 empty] | 0,1,2 | [6 empty] | 0 | Reserved
239 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / | [6 empty] | / | Reserved
240 |  |  | Check Step | [12 empty] | W
241 |  |  | INV-Lng | [5 empty] | Inverter Longitude | [6 empty] | W | [10 empty] | Longitude
242 |  |  | INV-Lat | [5 empty] | Inverter Latitude | [6 empty] | W | [10 empty] | Latitude
…… | [26 empty] | Reserved
303 | [26 empty] | Reserved
304 |  |  | uwAntiBackf lowFailPowe rLimitEE | [5 empty] | Anti-backflow failure power percentage | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1% |  |  |  |  | Anti-backflow failure default setting power percentage
305 |  |  | Qloadspeed | [5 empty] | Reactive loading speed | [6 empty] | R/W |  |  | 0-100 |  |  | 1% |  |  |  |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value
306 |  |  | bParallelAnti BackflowEna ble | [5 empty] | ParallelAnti-Backflow Enable | [6 empty] | R/W |  |  | 0-1 | [7 empty] | Parallel anti-Backflow open enable bit 1: enable 0:disable
307 |  |  | uwAntiBackf lowFailureRe sponseTime | [5 empty] | AntiBackflowFailure ResponseTime | [6 empty] | R/W |  |  | 1-5000 |  |  | 1s |  |  |  |  | AntiBackflow Failure Response Time
308 |  |  | uwParallelAn tiBackflowPo werLimitEE | [5 empty] | ParallelAntiBackflowPo wer | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1% |  |  |  |  | Parallel AntiBackflow Power
limit value setting
309 |  |  | bISOCheckC md | [5 empty] | ISO detection command | [6 empty] | R/W |  |  | 0-1 |  |  | 1 |  |  |  |  | ISO detection command
310 |  |  | bGPRSStatus | [5 empty] | GPRS Status 1: module not working 2: no sim card 3: No internet 4. TCP not connecting to server 5. TCP connection succeeded | [6 empty] | R/W |  |  | 0-255 |  |  | 1
311 |  |  | uwQmax_In ductive | [5 empty] | The inductive Qmax of the Q(V) curve | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
312 |  |  | uwQmax_Ca | [5 empty] | The Capactive Qmax of | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
|  |  | pactive | [5 empty] | the Q(V) curve
313 |  |  | uwReactiveP owerAdjustF ailureRespon seTime | [5 empty] | ReactivePowerAdjust Failur ResponseTime | [6 empty] | R/W |  |  | 0-5000 |  |  | S
314 |  |  | bSuperAntiB ackflowEnab le | [5 empty] | SuperAntiBackflow Enable | [6 empty] | R/W | [10 empty] | 0：disable，1：enable
315 |  |  | uwReactiveP owerStableT ime | [5 empty] | ReactivePowerStableTi me | [6 empty] | R/W |  |  | 0-200 |  |  | S
316 |  |  | uwQpStable Time | [5 empty] | QpStableTime | [6 empty] | R/W |  |  | 0-200 |  |  | S
317 |  |  | uwPuDerate Time | [5 empty] | PuDerateTime | [6 empty] | R/W |  |  | 0-200 |  |  | S
318 |  |  | uwQVModel Q2Point | [5 empty] | QV mode Q2 set point reactive power percentage | [6 empty] | R/W |  |  | 0-2000 |  |  | 0.1% |  |  |  |  | Capacitive 30% （ The corresponding setting is 700)； Inductive 30% (The corresponding setting is 1300)； used for IEE1547
319 |  |  | uwQVModel Q3Point | [5 empty] | QV mode Q3 set point reactive power percentage | [6 empty] | R/W |  |  | 0-2000 |  |  | 0.1%
320 |  |  | bVrefModel Enable | [5 empty] | VrefModelEnable | [6 empty] | R/W |  |  | 0 ： Vref mode for QV curve is not active 1 ： Vref mode for QV curve is active | [7 empty] | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted; When Vref mode is activated, V1~V4 of the QV curve are determined with Vref and cannot be changed, and Q1~Q4 can be modified by the host computer .used for IEE1547
321 |  |  | uwVrefMod elFilterTime | [5 empty] | VrefModelFilterTime | [6 empty] | R/W |  |  | 0-5000 |  |  | S |  |  |  |  | Activate Vref mode, the output filter value is equal to Vref with in the set time .used for IEE1547
322 |  |  | uwUserQPM odeP1Krate | [5 empty] | Active power P1 set point percentage for QP mode | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1% |  |  |  |  | used for IEE1547
323 |  |  | uwUserQPM odeP2Krate | [5 empty] | Active power P2 set point percentage for QP mode | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1% |  |  |  |  | used for IEE1547
324 |  |  | uwUserQPM odeP3Krate | [5 empty] | Active power P3 set point percentage for QP mode | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1% |  |  |  |  | used for IEE1547
325 |  |  | uwUserQPM odeQ1Krate | [5 empty] | Reactive power Q1 set point percentage for QP mode | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
326 |  |  | uwUserQPM odeQ2Krate | [5 empty] | Reactive power Q2 set point percentage for QP mode | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
327 |  |  | uwUserQPM odeQ3Krate | [5 empty] | Reactive power Q3 set point percentage for QP mode | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
328 |  |  | uwAcVoltHig hDeratPowe rLimit | [5 empty] | AcVoltHighDeratPower Limit | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
329 |  |  | BackflowSin gleCtrl | [5 empty] | BackflowSingleCtrl | [6 empty] | R/W |  |  | 0: disable 1: enable
330 |  |  | bAntiBackflo wProtectMo de | [5 empty] | AntiBackflowProtectM ode | [6 empty] | R/W |  |  | 0-3 | [7 empty] | Used for Australian
331 |  |  | uwUnderFU ploadZeroPo werPoint | [5 empty] | UnderfreqUploadZeroP owerPoint | [6 empty] | W | [5 empty] | 0.01H Z
332 |  |  | FreqDerateZ eroPowerPoi nt | [5 empty] | FreqDerateZeroPowerP oint | [6 empty] | W | [5 empty] | 0.01H Z
333 |  |  | bFreqDerati ngStopMode Enable | [5 empty] | FreqDeratingStopMode Enable | [6 empty] | R/W |  |  | 0-1
334 |  |  | bFreqIncreas ingEnable | [5 empty] | FreqIncreasingEnable | [6 empty] | R/W |  |  | 0-1
335 |  |  | uwFreqIncre asingRecove rTime | [5 empty] | FreqIncreasingRecover Time | [6 empty] | R/W | [5 empty] | 50ms
336 |  |  | uwFreqIncre asingEndLow | [5 empty] | FreqIncreasingEndLow Point | [6 empty] | R/W | [5 empty] | 0.01H Z
Point
337 |  |  | bFreqIncreas ingStopMod eEnable | [5 empty] | FreqIncreasingStopMo deEnable | [6 empty] | R/W |  |  | 0-1
338 |  |  | uwUserQpC hrP1Krate | [5 empty] | User QP function, charge P1 set point percentage | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
339 |  |  | uwUserQpC hrP2Krate | [5 empty] | User QP function, charge P2 set point percentage | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
340 |  |  | uwUserQpC hrP3Krate | [5 empty] | User QP function, charge P3 set point percentage | [6 empty] | R/W |  |  | 0-1000 |  |  | 0.1%
341 |  |  | wUserQpChr Q1Krate | [5 empty] | User QP function, charge Q1 set point percentage | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
342 |  |  | wUserQpChr Q2Krate | [5 empty] | User QP function, charge Q2 set point percentage | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
343 |  |  | wUserQpChr Q3Krate | [5 empty] | User QP function, charge Q3 set point percentage | [6 empty] | R/W |  |  | -1000-10 00 |  |  | 0.1% |  |  |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
344 |  |  | uwFreqDerat ingRecoverL owPoint | [5 empty] | FreqDeratingRecoverLo wPoint | [6 empty] | R/W | [5 empty] | 0.01H Z
345 |  |  | uwFreqIncre asingRecove rHighPoint | [5 empty] | FreqIncreasingRecover HighPoint | [6 empty] | R/W | [5 empty] | 0.01H Z
…….
532 |  |  | TurnOffUnlo adSpeed | [5 empty] | TurnOffUnloadSpeed | [6 empty] | W/R |  |  | 0-1000 | [6 empty] | 0.1% | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min
533 |  |  | LimitDevice | [5 empty] | Anti-backflow equipment selection | [6 empty] | W/R |  |  | 0-3 | [7 empty] | 1：Meter 3:CT
other meaningless
534 |  |  | PowerSetOn DCSourceMo de | [5 empty] | Power settings in dc source mode | [6 empty] | W/R |  |  | 0-90000 | [7 empty] | The unit is W
535 |  |  | OUFreqGrad e1En | [5 empty] | Over-under-frequency | [6 empty] | W/R |  |  | 0-1 | [7 empty] | 0:disable 1:enable
Grade1Enable,
currently only used by
CEI0-21
536 |  |  | Country Set | [5 empty] | Country settings under the same safety regulations | [6 empty] | W/R |  |  | 0-200 | [7 empty] | For mobile APP use only
538 |  |  | InterlockEna ble | [5 empty] | Three-machine communication Interlock function mode | [6 empty] | W/R |  |  | 0-2 | [7 empty] | 0：disable
1: Slave Enable 2. host enable
539 |  |  | OvTemperDe ratePoint | [5 empty] | Over temperature derate point | [6 empty] | W/R
540 |  |  | SafetySetPas sword | [5 empty] | Switch between different safety regulations to set the password | [6 empty] | W/R
541 |  |  | AFCI Onoff | [5 empty] | AFCI Onoff | [6 empty] | W/R |  |  | 0xA0/0xA 5 | [7 empty] | 0xA0：AFCI off 0xA5：AFCI on
542 |  |  | AfciSelfChec k | [5 empty] | AfciSelfCheck | [6 empty] | W/R | [10 empty] | 0：No self check 1: self check
543 |  |  | AfciReset | [5 empty] | AfciReset | [6 empty] | W/R | [10 empty] | 0：Not Reset 1: Reset
544 |  |  | AFCIValue1 | [5 empty] | AFCIThresholdValue （low） | [6 empty] | W/R |  |  | 0-65000
545 |  |  | AFCIValue2 | [5 empty] | AFCIThresholdValue （middle） | [6 empty] | W/R |  |  | 0-65000
546 |  |  | AFCIValue3 | [5 empty] | AFCIThresholdValue （High） | [6 empty] | W/R |  |  | 0-65000
547 |  |  | OverThresho ldValueMaxC nt | [5 empty] | OverThresholdValueMa xCnt | [6 empty] | W/R |  |  | 0-255
548 |  |  | AFCIScanTyp eEnable | [5 empty] | AFCI curve scan type | [6 empty] | W/R |  |  | 1~4 | [7 empty] | 1：A road strength
2：A road FFT value 3：B road strength 4：B road FFT value
549 |  |  | PowerVoltSt opModeEn | [5 empty] | PowerVoltStopModeEn | [6 empty] | W/R |  |  | 0、1 | [7 empty] | 0：disable 1:enable
The power is restored when the voltage is less than the recovery point
550 |  |  | VoltWattRec overTime | [5 empty] | Voltage active power recovery time | [6 empty] | W/R |  |  | 0-15000 |  |  | 20ms
551 |  |  | HVoltDerate | [5 empty] | Voltage active cut-off | [6 empty] | W/R |  |  | -5000-11
|  |  | StopPower | [5 empty] | power | [9 empty] | 400
552 |  |  | QVTimeExpo nent | [5 empty] | QVTimeExponent | [6 empty] | WR |  |  | 1-255 | [7 empty] | Q varies exponentially with time
553 |  |  | Volt-Watt Watt1 | [5 empty] | Voltage active V1 point, corresponding active power | [6 empty] | WR |  |  | 0-11400
554 |  |  | Volt-Watt Watt2 | [5 empty] | Voltage active V2 point, corresponding active power | [6 empty] | WR |  |  | 0-11400
……
600 |  |  | Volt-Var Var1 | [5 empty] | Voltage reactive V1 point, Corresponding reactive power percentage(Capacitive | [6 empty] | WR |  |  | 0-1000 | [7 empty] | 0%~100.0%,US latest safety regulations
Qmax)
601 |  |  | Volt-Var Var2 | [5 empty] | Voltage reactive V2 point, Corresponding reactive power percentage | [6 empty] | WR |  |  | 0-1000 | [7 empty] | 0%~100.0%,US latest safety regulations
602 |  |  | Volt-Var Var3 | [5 empty] | Voltage reactive V3 point, Corresponding reactive power percentage | [6 empty] | WR |  |  | 0-1000 | [7 empty] | 0%~100.0%,US latest safety regulations
603 |  |  | Volt-Var Var4 | [5 empty] | Voltage reactive V4 point, Corresponding reactive power percentage(Inductive Qmax) | [6 empty] | WR |  |  | 0-1000 | [7 empty] | 0%~100.0%,US latest safety regulations
604
605 |  |  | OPModEner gize | [5 empty] | Allowed inverter output power | [6 empty] | R/W |  |  | 0/1 | [7 empty] | 0: output power not allowed 1: allowable output power For US models
608 |  |  | OneKeySetB DCMode | [5 empty] | One key to set battery mode function | [6 empty] | R/W | [10 empty] | 0: self-use 1: battery priority 2: Grid priority 255：Disable Currently used for US models
609 |  |  | PowerOutpu tEnable | [5 empty] | Zero Power Output Enable | [17 empty] | 0：Zero Power Output
1：Unlimited output power (default is 1)
610 |  |  | DealDebugP araFlag | [5 empty] | Flag bit for clearing debug variables | [17 empty] | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear
612 |  |  | bAcCoupleE n | [5 empty] | AcCoupleEn | [6 empty] | R/W |  |  | 0-1 | [7 empty] | 0：disable 1：enable
…..
660 |  |  | ReloadCmd | [5 empty] | M3 remote command | [17 empty] | 0xA0: Initialize safety defaults 0xAA: Reboot M3 remotely
Six group for Storage Power
Register NO. |  |  | Variable Name | [5 empty] | Description | [6 empty] | Write or not |  |  | Value |  |  | Unit |  |  |  | Initial value | Note
1000 |  |  | Float charge current limit | [5 empty] | When charge current battery need is lower than this value, enter into float charge | [6 empty] | W | [5 empty] | 0.1A |  |  |  | 600 | CC current
1001 |  |  | PF CMD memory state | [5 empty] | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. | [6 empty] | W |  |  | 0or1, | [6 empty] | 0 | Means these settings will be acting or not when next power on(02 repeat)
1002 |  |  | VbatStartF orDischarg e | [5 empty] | LV Vbat | [6 empty] | R/W | [5 empty] | 0.1V |  |  |  |  | Lead-acid battery LV voltage
1003 |  |  | VbatlowWa rnClr | [5 empty] | LoadPercent(only lead-Acid): 45.5V <20% 48.0V 20%~50% 49.0V >50 | [6 empty] | W | [5 empty] | 0.1V |  |  |  |  | Clear battery low voltage error voltage point
1004 |  |  | Vbatstopfo rdischarge | [5 empty] | Should stop discharge when lower than this | [6 empty] | W | [5 empty] | 0.01V
voltage(only lead-Acid): 46.0V <20% 44.8V 20%~50% 44.2V >50%
1005 |  |  | Vbat stop for charge | [5 empty] | Should stop charge when higher than this voltage | [6 empty] | W | [5 empty] | 0.01V |  |  |  | 5800
1006 |  |  | Vbat start for discharge | [5 empty] | Should not discharge when lower than this voltage | [6 empty] | W | [5 empty] | 0.01V |  |  |  | 4800
1007 |  |  | Vbat constant charge | [5 empty] | can charge when lower than this voltage | [6 empty] | W | [5 empty] | 0.01V |  |  |  | 5800 | CV voltage（acid）
1008 |  |  | EESysInfo.S ysSetEn | [5 empty] | Bit0：Resved; Bit1：Resved; Bit2：Resved; Bit3：Resved; Bit4：Resved; Bit5：bDischargeEn； Bit6：ForceDischrEn； Bit7：ChargeEn； Bit8：bForceChrEn； Bit9：bBackUpEn； Bit10：bInvLimitLoadE； Bit11：bSpLimitLoadEn； Bit12：bACChargeEn； Bit13：bPVLoadLimitEn; Bit14,15:UnUsed; | [6 empty] | W | [10 empty] | System Enable
1009 |  |  | Battemp lower limit d | [5 empty] | Battery temperature lower limit for discharge | [6 empty] | W |  |  | 0-200:0-2 0℃ 1000-140 0：-40-0℃ |  |  | 0.1℃ |  |  |  | 1170
1010 |  |  | Bat temp upper limit d | [5 empty] | Battery temperature upper limit for discharge | [6 empty] | W |  |  | 200-1000 |  |  | 0.1℃ |  |  |  | 420
1011 |  |  | Bat temp lower limit c | [5 empty] | Battery temperature lower limit for charge | [6 empty] | W |  |  | 0-200:0-2 0℃ 1000-140 0：-40-0℃ |  |  | 0.1℃ |  |  |  | 30 | Lower temperature limit
1012 |  |  | Bat temp upper limit c | [5 empty] | Battery temperature upper limit for charge | [6 empty] | W |  |  | 200-1000 |  |  | 0.1℃ |  |  |  | 370 | Upper temperature limit
1013 |  |  | uwUnderFr eDischarge DelyTime | [5 empty] | Under Fre Delay Time | [6 empty] | s |  |  | 0-20 |  |  | 50ms |  |  |  |  | Under Fre Delay Time
1014 |  |  | BatMdlSeri alNum | [5 empty] | Battery serial number | [6 empty] | W |  |  | 00:00 | [7 empty] | SPH4-11K used
1015 |  |  | BatMdlPara llNum | [5 empty] | Battery parallel section | [6 empty] | W |  |  | 00:00 | [7 empty] | SPH4-11K used
1016 |  |  | DRMS_EN | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | 0：disable 1：enable
1017 |  |  | Bat First Start Time 4 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1018 |  |  | Bat First Stop Time 4 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1019 |  |  | BatFirst on/off Switch 4 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Battery priority enable 1
1020 |  |  | Bat First Start Time 5 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1021 |  |  | Bat First Stop Time 5 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1022 |  |  | BatFirst on/off Switch 5 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Battery priority enable 1
1023 |  |  | Bat First Start Time 6 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1024 |  |  | Bat First Stop Time 6 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1025 |  |  | BatFirst on/off Switch 6 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Battery priority enable 1
1026 |  |  | Grid First Start Time | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
4
1027 |  |  | Grid First Stop Time 4 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1028 |  |  | Grid First Stop Switch 4 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Grid priority enable
1029 |  |  | Grid First Start Time 5 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1030 |  |  | Grid First Stop Time 5 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1031 |  |  | Grid First Stop Switch 5 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Grid priority enable
1032 |  |  | Grid First Start Time 6 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1033 |  |  | Grid First Stop Time 6 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1034 |  |  | Grid First Stop Switch 6 | [5 empty] | Enable:1 Disable:0 | [9 empty] | 0 or 1 | [7 empty] | Grid priority enable
1035 |  |  | Bat First Start Time 4 | [5 empty] | High eight:hours Low eight: minutes | [9 empty] | 0-23 0-59
1036 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1037 |  |  | bCTMode | [5 empty] | Use the CTMode to Choose RFCT \ Cable CT\METER | [6 empty] | W |  |  | 2:METER 1:cWirele ssCT 0:cWiredC T | [6 empty] | 0
1038 |  |  | CTAdjust | [5 empty] | CTAdjust enable | [6 empty] | W |  |  | 0:disable 1:enable | [6 empty] | 0
1039 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1040 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1041 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1042 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  |  | Reserve
1043 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1044 |  |  | Priority | [5 empty] | ForceChrEn/ForceDischr En Load first/bat first /grid first | [6 empty] | R |  |  | 0.Load(de fault)/1.B attery/2.G rid | [7 empty] | bForceChrEn/disbForceDischrE n/dis
1045 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1046 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1047 |  |  | AgingTestSt ep Cmd | [5 empty] | Command for aging test | [9 empty] | 0: default 1: charge 2: discharge | [7 empty] | Cmd for aging test
1048 |  |  | BatteryTyp e | [5 empty] | Battery type choose of buck-boost input | [9 empty] | 0:Lithium 1:Lead-aci d 2:other | [6 empty] | 0 | Battery type
1049 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  |  | Reserve
1050 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1051 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  |  | Reserve
1052 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  |  | Reserve
1053 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  |  | Reserve
1054 |  |  | / | [5 empty] | / | [6 empty] | / |  |  | / |  |  | / |  |  |  | / | Reserve
1060 |  |  | BuckUpsFunE n | [7 empty] | Ups function enable or disable | [9 empty] | 0:disable 1:enable
1061 |  |  | BuckUPSVoltS et | [7 empty] | UPS output voltage | [9 empty] | 0:230 1:208 2:240 | [5 empty] | 230V
1062 |  |  | UPSFreqSet | [7 empty] | UPS output frequency | [9 empty] | 0:50Hz 1:60Hz | [5 empty] | 50Hz
... |  |  | / | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  | reverse
Priority set
1070 |  |  | GridFirstDisch argePowerRat e | [7 empty] | Discharge Power Rate when Grid First | [7 empty] | W |  | 0-100 |  |  | 1% |  |  | Discharge Power Rate when Grid First
1071 |  |  | GridFirstStopS OC | [7 empty] | Stop Discharge soc when Grid First | [7 empty] | W |  | 0-100 |  |  | 1% |  |  | Stop Discharge soc when Grid First
1072… 1079 |  |  | / | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  |  | reverse
1080 |  |  | Grid First Start Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1081 |  |  | Grid First Stop Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1082 |  |  | Grid First Stop Switch 1 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Grid First enable
1083 |  |  | Grid First Start Time 2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1084 |  |  | Grid First Stop Time 2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1085 |  |  | Grid First Stop Switch 2 | [7 empty] | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 | [9 empty] | 0 or 1 | [5 empty] | Grid First enable |  |  |  |  | ForceDischarge; LCD_SET_FORCE_T RUE_2
1086 |  |  | Grid First Start Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1087 |  |  | Grid First Stop Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1088 |  |  | Grid First Stop Switch 3 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Grid First enable
1089 |  |  | / | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  |  | reserve
1090 |  |  | BatFirstPower Rate | [7 empty] | Charge Power Rate when Bat First | [7 empty] | W |  | 0-100 |  |  | 1% |  |  | Charge Power Rate when Bat First
1091 |  |  | wBatFirst stop SOC | [7 empty] | Stop Charge soc when Bat First | [7 empty] | W |  | 0-100 |  |  | 1% |  |  | Stop Charge soc when Bat First
1092 |  |  | AC charge Switch | [7 empty] | When Bat First Enable:1 Disable:0 | [9 empty] | Enable:1 Disable:0 | [5 empty] | AC Charge Enable
1093… 1099
1100 |  |  | Bat First Start Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1101 |  |  | Bat First Stop Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1102 |  |  | BatFirst on/off Switch 1 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Bat First Enable1
1103 |  |  | Bat First Start Time 2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1104 |  |  | Bat First Stop Time 2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1105 |  |  | BatFirston/off Switch 2 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Bat First Enable2
1106 |  |  | Bat First Start Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1107 |  |  | Bat First Stop Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59
1108 |  |  | BatFirston/off Switch 3 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Bat First Enable3
1109 |  |  | / | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  |  | reserve
1110 |  |  | Load First Start Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1111 |  |  | Load First Stop Time 1 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1112 |  |  | Load First Switch 1 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Load First Enable |  |  |  |  | SPA/ reserve
1113 |  |  | Load First Start Time2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1114 |  |  | Load First Stop Time 2 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1115 |  |  | Load First Switch 2 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Load First Enable |  |  |  |  | SPA/ reserve
1116 |  |  | Load First Start Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1117 |  |  | Load First Stop Time 3 | [7 empty] | High eight bit：hour Low eight bit：minute | [9 empty] | 0-23 0-59 | [10 empty] | SPA/ reserve
1118 |  |  | Load First Switch 3 | [7 empty] | Enable :1 Disable:0 | [9 empty] | 0 or 1 | [5 empty] | Load First Enable |  |  |  |  | SPA/ reserve
1119 |  |  | NewEPowerC alcFlag | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  |  | 0：The old formula 1 ： The new formula
1120 |  |  | BackUpEn | [7 empty] | BackUp Enable | [20 empty] | MIX US
1121 |  |  | SGIPEn | [7 empty] | SGIP Enable | [20 empty] | MIX US
……… |  |  | 1122~1124 | [7 empty] | / | [7 empty] | / |  | / |  |  | / |  |  | / |  |  |  |  | reserve
1125 |  |  | BatSerialNO. 8 | [7 empty] | Product serial number of the first PACK of energy storage batteries | [7 empty] | / |  | / |  |  | ASCII
1126 |  |  | BatSerialNO. 7 | [15 empty] | / |  | / |  |  | ASCII
1127 |  |  | BatSerialNO. 6 | [15 empty] | / |  | / |  |  | ASCII
1128 |  |  | BatSerialNO. 5 | [15 empty] | / |  | / |  |  | ASCII
1129 |  |  | BatSerialNO. 4 | [15 empty] | / |  | / |  |  | ASCII
1130 |  |  | BatSerialNO. 3 | [15 empty] | / |  | / |  |  | ASCII
1131 |  |  | BatSerialNO. 2 | [15 empty] | / |  | / |  |  | ASCII
1132 |  |  | BatSerialNO. 1 | [15 empty] | / |  | / |  |  | ASCII
1132 ~1204 |  |  | BatSerialNO. 8~ BatSerialNO. 1 | [7 empty] | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and | [7 empty] | / |  | / |  |  | ASCII
the format of the serial number of each PACK is 1125 to 1132
……
1244 |  |  | Com version NameH | [7 empty] | Name of the battery main control firmware version | [12 empty] | ASCII
1245 |  |  | Com version NameL | [7 empty] | Name of the battery main control firmware version | [12 empty] | ASCII
1246 |  |  | Com version No | [7 empty] | Version of the battery main control firmware | [12 empty] | digital
1247 |  |  | Com version NameH | [7 empty] | Name of battery monitoring firmware version | [12 empty] | ASCII
1248 |  |  | Com version NameL | [7 empty] | Name of battery monitoring firmware version | [12 empty] | ASCII
1249 |  |  | Com version No | [7 empty] | Battery monitoring firmware version | [12 empty] | digital
Use for TL-X and TL-XH
3000 |  |  | ExportLimitFa iledPowerRat e | [7 empty] | The power rate when exportLimit failed | [7 empty] | R/W |  |  |  |  | 0.1% | [7 empty] | The power rate when exportLimit failed
3001 |  |  | New Serial NO | [7 empty] | Serial number 1-2 | [7 empty] | R/W |  |  |  |  | ASCII | [7 empty] | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters.
3002 |  |  | New Serial NO | [7 empty] | Serial number 3-4 | [7 empty] | R/W |  |  |  |  | ASCII
3003 |  |  | New Serial NO | [7 empty] | Serial number 5-6 | [7 empty] | R/W |  |  |  |  | ASCII
3004 |  |  | New Serial NO | [7 empty] | Serial number 7-8 | [7 empty] | R/W |  |  |  |  | ASCII
3005 |  |  | New Serial NO | [7 empty] | Serial number 9-10 | [7 empty] | R/W |  |  |  |  | ASCII
3006 |  |  | New Serial NO | [7 empty] | Serial number 11-12 | [7 empty] | R/W |  |  |  |  | ASCII
3007 |  |  | New Serial NO | [7 empty] | Serial number 13-14 | [7 empty] | R/W |  |  |  |  | ASCII
3008 |  |  | New Serial NO | [7 empty] | Serial number 15-16 | [7 empty] | R/W |  |  |  |  | ASCII
3009 |  |  | New Serial NO | [7 empty] | Serial number 17-18 | [7 empty] | R/W |  |  |  |  | ASCII
3010 |  |  | New Serial NO | [7 empty] | Serial number 19-20 | [7 empty] | R/W |  |  |  |  | ASCII
3011 |  |  | New Serial NO | [7 empty] | Serial number 21-22 | [7 empty] | R/W |  |  |  |  | ASCII
3012 |  |  | New Serial NO | [7 empty] | Serial number 23-24 | [7 empty] | R/W |  |  |  |  | ASCII
3013 |  |  | New Serial NO | [7 empty] | Serial number 25-26 | [7 empty] | R/W |  |  |  |  | ASCII
3014 |  |  | New Serial NO | [7 empty] | Serial number 27-28 | [7 empty] | R/W |  |  |  |  | ASCII
3015 |  |  | New Serial NO | [7 empty] | Serial number 29-30 | [7 empty] | R/W |  |  |  |  | ASCII
3016 |  |  | DryContactFu ncEn | [7 empty] | DryContact function enable | [7 empty] | R/W |  | 0:Disable 1: Enable | [10 empty] | DryContact function enable
3017 |  |  | DryContactOn Rate | [7 empty] | The power rate of drycontact turn on | [7 empty] | R/W |  | 0~1000 |  |  | 0.1% | [7 empty] | The power rate of drycontact turn on
3018 |  |  | bWorkMode | [7 empty] | WorkMode 0:default,1: System Retrofit 2: Multi-Parallel | [7 empty] | R/W |  | 0、1、2 | [10 empty] | MIN2.5~6KTL-XH/ XA Double CT special
3019 |  |  | DryContactOf fRate | [7 empty] | DryContactOffRate | [7 empty] | Dry contact closure power |  | R/W |  |  | 0~100 0 |  |  | 0.1% |  |  |  |  | Dry contact closure power pe rcentage
3020 |  |  | BoxCtrlInvOrd er | [7 empty] | BoxCtrlInvOrder | [7 empty] | Off-net box control instruct ion |  | R/W
3021 |  |  | ExterCommOf fGridEn | [7 empty] | External communication setting manual off-network enable | [7 empty] | R/W | [12 empty] | 0x00: Disable; （default） 0x01: Enable;
3022 |  |  | uwBdcStopW orkOfBusVolt | [7 empty] | BdcStopWorkOfBusVolt | [7 empty] | R
3023 |  |  | bGridType | [7 empty] | GridType---0:SinglePhase 1:ThreePhase 2:SplitPhase | [7 empty] | R/W |  | 0、1、2 | [10 empty] | MIN2.5~6KTL-XH/ XA Double CT special
3024 |  |  | Float charge current limit | [7 empty] | When charge current battery need is lower than | [7 empty] | R/W |  |  |  |  | 0.1A |  |  | 600 |  |  |  |  | CC current
this value, enter into float charge
3025 |  |  | VbatWarning | [7 empty] | "Battery-low" warning setup voltage | [7 empty] | R/W |  |  |  |  | 0.1V |  |  | 4800 |  |  |  |  | Lead acid battery LV voltage
3026 |  |  | VbatlowWarn Clr | [7 empty] | "Battery-low" warning clear voltage | [7 empty] | R/W |  |  |  |  | 0.1V | [7 empty] | Clear battery low voltage error voltage point LoadPercent(only lead-Acid): 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%);
3027 |  |  | Vbatstopfordi scharge | [7 empty] | Battery cut off voltage | [7 empty] | R/W |  |  |  |  | 0.1V | [7 empty] | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%);
3028 |  |  | Vbat stop for charge | [7 empty] | Battery over charge voltage | [7 empty] | R/W |  |  |  |  | 0.01V |  |  | 5800 |  |  |  |  | Should stop charge when higher than this voltage
3029 |  |  | Vbat start for discharge | [7 empty] | Battery start discharge voltage | [7 empty] | R/W |  |  |  |  | 0.01V |  |  | 4800 |  |  |  |  | Should not discharge when lower than this voltage
3030 |  |  | Vbat constant charge | [7 empty] | Battery constant charge voltage | [7 empty] | R/W |  |  |  |  | 0.01V |  |  | 5800 |  |  |  |  | CV voltage（acid） can charge when lower than this voltage
3031 |  |  | Battemp lower limit d | [7 empty] | Battery temperature lower limit for discharge | [7 empty] | R/W |  |  |  |  | 0.1℃ |  |  | 1170 |  |  |  |  | 0-200:0-20℃ 1000-1400： -40-0℃
3032 |  |  | Bat temp upper limit d | [7 empty] | Battery temperature upper limit for discharge | [7 empty] | R/W |  |  |  |  | 0.1℃ |  |  | 420
3033 |  |  | Bat temp lower limit c | [7 empty] | Battery temperature lower limit for charge | [7 empty] | R/W |  |  |  |  | 0.1℃ |  |  | 30 |  |  |  |  | Battery temperature lower limit 0-200:0-20℃ 1000-1400： -40-0℃
3034 |  |  | Bat temp upper limit c | [7 empty] | Battery temperature upper limit for charge | [7 empty] | R/W |  |  |  |  | 0.1℃ |  |  | 370 |  |  |  |  | Battery temperature upper limit
3035 |  |  | uwUnderFreD ischargeDelyT ime | [7 empty] | Under Fre Delay Time | [7 empty] | R/W |  |  |  |  | 50ms | [7 empty] | Under Fre Delay Time
3036 |  |  | GridFirstDisch argePowerRat e | [7 empty] | Discharge Power Rate when Grid First | [15 empty] | 1-255
3037 |  |  | GridFirstStopS OC | [7 empty] | Stop Discharge soc when Grid First | [15 empty] | 1-100
3038 |  |  | Time 1(xh) | [7 empty] | Period 1: [Start Time ~ End Time], [Charge/Discharge], [Disable/Enable] 3038 enable, charge and discharge, start time, end time 3039 | [7 empty] | R/W | [12 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled;
3039 | [18 empty] | R/W | [12 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3040 |  |  | Time 2(xh) | [7 empty] | Time period 2: [start time ~ end time], [charge / discharge], [disable / enable] 3040 enable, charge and discharge, start time, 3041 end time | [7 empty] | R/W | [12 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1:
enabled;
3041 | [18 empty] | R/W | [12 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3042 |  |  | Time 3(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3043 | [18 empty] | R/W | [12 empty] | With Time1
3044 |  |  | Time 4(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3045 | [18 empty] | R/W | [12 empty] | With Time1
3046 |  |  | 预留
3047 |  |  | BatFirstPower Rate | [7 empty] | Charge Power Rate when Bat First | [15 empty] | 1-100
3048 |  |  | wBatFirst stop SOC | [7 empty] | Stop Charge soc when Bat First | [15 empty] | 1-100
3049 |  |  | AcChargeEna ble | [7 empty] | AcChargeEnable | [20 empty] | Enable :1 Disable:0
3050 |  |  | Time 5(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3051 | [18 empty] | R/W | [12 empty] | With Time1
3052 |  |  | Time 6(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3053 | [18 empty] | R/W | [12 empty] | With Time1
3054 |  |  | Time 7(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3055 | [18 empty] | R/W | [12 empty] | With Time1
3056 |  |  | Time 8(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3057 | [18 empty] | R/W | [12 empty] | With Time1
3058 |  |  | Time 9(xh) | [7 empty] | With Time1 | [7 empty] | R/W | [12 empty] | With Time1
3059 | [18 empty] | R/W | [12 empty] | With Time1
3060~ 3069 |  |  | Reserved
3070 |  |  | BatteryType | [7 empty] | Battery type choose of buck-boost input | [7 empty] | R/W | [12 empty] | Battery type 0:Lithium 1:Lead-acid 2:other
3071 |  |  | BatMdlSeria/ ParalNum | [7 empty] | BatMdlSeria/ParalNum | [7 empty] | R/W | [12 empty] | BatMdlSeria/Paral Num; SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits indicate the number of parallel sections;
3072 |  |  | Reserved
3073 |  |  | Reserved
3074 |  |  | Reserved
3075 |  |  | Reserved
3076 |  |  | Reserved
3077 |  |  | Reserved
3078 |  |  | Reserved
3079 |  |  | UpsFunEn | [7 empty] | Ups function enable or disable | [7 empty] | R/W | [7 empty] | 0 |  |  |  |  | 0:disable 1:enable
3080 |  |  | UPSVoltSet | [7 empty] | UPS output voltage | [7 empty] | R/W | [7 empty] | 0 |  |  |  |  | 0:230V 1:208V 2:240V
3081 |  |  | UPSFreqSet | [7 empty] | UPS output frequency | [7 empty] | R/W | [7 empty] | 0 |  |  |  |  | 0:50Hz 1:60Hz
3082 |  |  | bLoadFirstSto pSocSet | [7 empty] | StopSoc When LoadFirst | [7 empty] | R/W | [7 empty] | 13-100 |  |  |  |  | ratio
3083 |  |  | Reserved
3084 |  |  | Reserved
3085 |  |  | Com Address | [7 empty] | Communication addr | [7 empty] | R/W | [7 empty] | 1 |  |  |  |  | 1 : Communication addr=1 1 ~ 254 : Communication addr=1~254
3086 |  |  | BaudRate | [7 empty] | Communication BaudRate | [7 empty] | R/W | [7 empty] | 0 |  |  |  |  | 0: 9600 bps 1: 38400 bps
3087 |  |  | Serial NO. 1 | [7 empty] | Serial Number 1-2 | [7 empty] | R/W |  |  |  |  | ASCII | [7 empty] | For battery
3088 |  |  | Serial NO. 2 | [7 empty] | Serial Number 3-4 | [7 empty] | R/W |  |  |  |  | ASCII
3089 |  |  | Serial NO. 3 | [7 empty] | Serial Number 5-6 | [7 empty] | R/W |  |  |  |  | ASCII
3090 |  |  | Serial NO. 4 | [7 empty] | Serial Number 7-8 | [7 empty] | R/W |  |  |  |  | ASCII
3091 |  |  | Serial No. 5 | [7 empty] | Serial Number 9-10 | [7 empty] | R/W |  |  |  |  | ASCII
3092 |  |  | Serial No.6 | [7 empty] | Serial Number 11-12 | [7 empty] | R/W |  |  |  |  | ASCII
3093 |  |  | Serial No. 7 | [7 empty] | Serial Number 13-14 | [7 empty] | R/W |  |  |  |  | ASCII
3094 |  |  | Serial No. 8 | [7 empty] | Serial Number 15-16 | [7 empty] | R/W |  |  |  |  | ASCII
3095 |  |  | BdcResetCmd | [7 empty] | BDC Reset command | [7 empty] | R/W | [12 empty] | 0：Invalid data 1：Reset setting parameters 2：Reset correction parameter 3：Clear historical power
3096 |  |  | ARKM3 Code | [7 empty] | BDCMonitoring software code | [7 empty] | R |  |  |  |  | ASCII | [7 empty] | ZEBA
3097
3098 |  |  | DTC | [7 empty] | DTC | [7 empty] | R
3099 |  |  | FW Code | [7 empty] | DSP software code | [7 empty] | R |  |  |  |  | ASCII
3100
3101 |  |  | Processor1 FW Vision | [7 empty] | DSP Software Version | [7 empty] | R |  |  |  |  | ASCII
3102 |  |  | BusVoltRef | [7 empty] | Minimum BUS voltage for charging and discharging batteries | [7 empty] | R
3103 |  |  | ARKM3Ver | [7 empty] | BDC monitoring software version | [7 empty] | R
3104 |  |  | BMS_MCUVer sion | [7 empty] | BMS hardware version information | [7 empty] | R |  | 1
3105 |  |  | BMS_FW | [7 empty] | BMS software version information | [7 empty] | R |  | 1
3106 |  |  | BMS_Info | [7 empty] | BMS ManufacturerName | [7 empty] | R |  | 1
3107 |  |  | BMSCommTy pe | [7 empty] | BMSCommType | [7 empty] | R |  | 1 | [10 empty] | BMSCommunicati on interface type： 0: RS485; 1: CAN;
3108 |  |  | Module 4 | [7 empty] | BDCmodel (4) | [7 empty] | R/W |  | &*11 | [10 empty] | SxxBxx
3109 |  |  | Module 3 | [7 empty] | BDCmodel (3) | [7 empty] | R/W |  | &*11 | [10 empty] | DxxTxx
3110 |  |  | Module 2 | [7 empty] | BDCmodel (2) | [7 empty] | R/W |  | &*11 | [10 empty] | PxxUxx
3111 |  |  | Module 1 | [7 empty] | BDCmodel (1) | [7 empty] | R/W |  | &*11 | [10 empty] | Mxxxx
3112 |  |  | Reserved
3113 |  |  | unProtocolVe r | [7 empty] | BDCProtocolVer | [7 empty] | R |  | 1 | [10 empty] | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed Bit0-bit7 Minor version number [0-256]. If the protocol is changed, you need to update this version No.
3114 |  |  | uwCertificatio nVer | [7 empty] | BDC CertificationVer | [7 empty] | R |  | 1
3115 ~ 3124 |  |  | Reserved
US Machine type Time Set
3125 |  |  | Time Month1 | [7 empty] | Use with Time1-9（us） ，Add month time | [7 empty] | R/W | [12 empty] | bit0~3:month_L； bit4~7: month_H bit8, 0:disable 1：enable Bit9~15:reserve
3126 |  |  | Time Month2 | [7 empty] | Use with Time10-18（us） ，Add month time | [7 empty] | R/W | [12 empty] | With Time Month1
3127 |  |  | Time Month3 | [7 empty] | Use with Time19-27（us） ，Add month time | [7 empty] | R/W | [12 empty] | With Time Month1
3128 |  |  | Time Month4 | [7 empty] | Use with Time28-36（us） ，Add month time | [7 empty] | R/W | [12 empty] | With Time Month1
3129 |  |  | Time 1（us） | [7 empty] | time1：[starttime~endtime] | [7 empty] | R/W |  | [Charge/ discharg e/counte r | [10 empty] | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst;
[21 empty] | current], [disable/ enable] | [10 empty] | 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0:disable; 1:enable;
3130 | [18 empty] | R/W | [12 empty] | bit0~6:min； bit7~11:hour； bit12-13, 0:Weekday 1:Weekend 2:WeeK bit14~15：reserve
3131-3 132 |  |  | Time 2（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3133-3 134 |  |  | Time 3（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3135-3 136 |  |  | Time 4（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3137-3 138 |  |  | Time 5（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3139-3 140 |  |  | Time 6（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3141-3 142 |  |  | Time 7（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3143-3 144 |  |  | Time 8（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3145-3 146 |  |  | Time9（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3147-3 148 |  |  | Time 10（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3149-3 150 |  |  | Time 11（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3151-3 152 |  |  | Time 12（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3153-3 154 |  |  | Time 13（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3155-3 156 |  |  | Time 14（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3157-3 158 |  |  | Time15（us） | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as Time 1 （us）
3159-3 160 3161-3 162 3163-3 164 3165-3 166 3167-3 168 3169-3 170 3171-3 172 3173-3 174 3175-3 176 3177-3 178 3179-3 180 3181-3 182 3183-3 184 3185-3 186 3187-3 188 3189-3 190 3191-3 192 3193-3 194 3195-3 196 3197-3 198 3199-3 200 |  |  | Time 16（us）Same as above Time 17（us）Same as above Time 18（us）Same as above Time 19（us）Same as above Time 20（us）Same as above Time 21（us）Same as above Time 22（us）Same as above Time 23（us）Same as above Time 24（us）Same as above Time 25（us）Same as above Time 26（us）Same as above Time 27（us）Same as above Time 28（us）Same as above Time 29（us）Same as above Time 30（us）Same as above Time 31（us）Same as above Time 32（us）Same as above Time 33（us）Same as above Time 34（us）Same as above Time 35（us）Same as above Time 36（us）Same as above | [11 empty] | R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W R/W |  |  |  |  | Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us） Same as Time 1 （us）
3201 |  |  | SpecialDay1 | [7 empty] | SpecialDay1（month，Day） | [7 empty] | R/W | [12 empty] | bit0~7:day； bit8~14:month bit15， 0：disable 1： enable
3202 |  |  | SpecialDay1_ Time1 | [7 empty] | Start time | [7 empty] | R/W | [12 empty] | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst; 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable;
3203 | [10 empty] | endtime | [7 empty] | R/W | [12 empty] | bit0~6:min； bit7~11:hour； bit12~15：reserve
3204-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
205 |  |  | Time2 | [28 empty] | SpecialDay1_Time
1
3206-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
207 |  |  | Time3 | [28 empty] | SpecialDay1_Time
1
3208-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
209 |  |  | Time4 | [28 empty] | SpecialDay1_Time
1
3210-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
211 |  |  | Time5 | [28 empty] | SpecialDay1_Time
1
3212-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
213 |  |  | Time6 | [28 empty] | SpecialDay1_Time
1
3214-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
215 |  |  | Time7 | [28 empty] | SpecialDay1_Time
1
3216-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
217 |  |  | Time8 | [28 empty] | SpecialDay1_Time
1
3218-3 |  |  | SpecialDay1_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
219 |  |  | Time9 | [28 empty] | SpecialDay1_Time
1
3220 |  |  | SpecialDay2 | [7 empty] | SpecialDay2（month，Day） | [7 empty] | R/W | [12 empty] | bit0~7:day； bit8~14:month bit15， 0：disable 1：enable
3221 |  |  | SpecialDay2_ Time1 | [7 empty] | Start time | [7 empty] | R/W | [12 empty] | bit0~6: min； bit7~11: hour； bit12~14, 0: loadfirst; 1: batfirst； 2: gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable;
3222 | [10 empty] | endtime | [7 empty] | R/W | [12 empty] | bit0~6: min； bit7~11: hour； bit12~15：reserve
3223-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
224 |  |  | Time2 | [28 empty] | SpecialDay2_Time
1
3225-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
226 |  |  | Time3 | [28 empty] | SpecialDay2_Time
1
3227-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
228 |  |  | Time4 | [28 empty] | SpecialDay2_Time
1
3229-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
230 |  |  | Time5 | [28 empty] | SpecialDay2_Time
1
3231-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
232 |  |  | Time6 | [28 empty] | SpecialDay2_Time
1
3233-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
234 |  |  | Time7 | [28 empty] | SpecialDay2_Time
1
3235-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
236 |  |  | Time8 | [28 empty] | SpecialDay2_Time
1
3237-3 |  |  | SpecialDay2_ | [7 empty] | Same as above | [7 empty] | R/W | [12 empty] | Same as
238 |  |  | Time9 | [28 empty] | SpecialDay2_Time
1
3239-3 249 |  |  |  | Reserve | [6 empty] | Reserve | [7 empty] | R/W
BDC information (support up to 10 parallel BDC)
5000-5039 | [10 empty] | 1 | [13 empty] | Reference 3085 to 3124 for a total of 40 registers Description
5040-5079 | [10 empty] | 2
5000+(N-1)*40--- 5039+(N-1)*40 | [10 empty] | N
4.2 Input Reg
NO. |  | Variable Name | [9 empty] | Description | [10 empty] | Value | [6 empty] | Unit |  |  |  |  | Note
First group
0 |  |  | Inverter Status | [8 empty] | Inverter run state | [10 empty] | 0:waiting, 1:normal, 3:fault
1 |  |  | Ppv H | [8 empty] | Input power (high) | [17 empty] | 0.1W
2 |  |  | Ppv L | [8 empty] | Input power (low) | [17 empty] | 0.1W
3 |  |  | Vpv1 | [8 empty] | PV1 voltage | [17 empty] | 0.1V
4 |  |  | PV1Curr | [8 empty] | PV1 input current | [17 empty] | 0.1A
5 |  |  | Ppv1 H | [8 empty] | PV1 input power(high) | [17 empty] | 0.1W
6 |  |  | Ppv1 L | [8 empty] | PV1 input power(low) | [17 empty] | 0.1W
7 |  |  | Vpv2 | [8 empty] | PV2 voltage | [17 empty] | 0.1V
8 |  |  | PV2Curr | [8 empty] | PV2 input current | [17 empty] | 0.1A
9 |  |  | Ppv2 H | [8 empty] | PV2 input power (high) | [17 empty] | 0.1W
10 |  |  | Ppv2 L | [8 empty] | PV2 input power (low) | [17 empty] | 0.1W
11 |  |  | Vpv3 | [8 empty] | PV3 voltage | [17 empty] | 0.1V
12 |  |  | PV3Curr | [8 empty] | PV3 input current | [17 empty] | 0.1A
13 |  |  | Ppv3 H | [8 empty] | PV3 input power (high) | [17 empty] | 0.1W
14 |  |  | Ppv3 L | [8 empty] | PV3 input power (low) | [17 empty] | 0.1W
15 |  |  | Vpv4 | [8 empty] | PV4 voltage | [17 empty] | 0.1V
16 |  |  | PV4Curr | [8 empty] | PV4 input current | [17 empty] | 0.1A
17 |  |  | Ppv4 H | [8 empty] | PV4 input power (high) | [17 empty] | 0.1W
18 |  |  | Ppv4 L | [8 empty] | PV4 input power (low) | [17 empty] | 0.1W
19 |  |  | Vpv5 | [8 empty] | PV5 voltage | [17 empty] | 0.1V
20 |  |  | PV5Curr | [8 empty] | PV5 input current | [17 empty] | 0.1A
21 |  |  | Ppv5H | [8 empty] | PV5 input power(high) | [17 empty] | 0.1W
22 |  |  | Ppv5 L | [8 empty] | PV5 input power(low) | [17 empty] | 0.1W
23 |  |  | Vpv6 | [8 empty] | PV6 voltage | [17 empty] | 0.1V
24 |  |  | PV6Curr | [8 empty] | PV6 input current | [17 empty] | 0.1A
25 |  |  | Ppv6 H | [8 empty] | PV6 input power (high) | [17 empty] | 0.1W
26 |  |  | Ppv6 L | [8 empty] | PV6 input power (low) | [17 empty] | 0.1W
27 |  |  | Vpv7 | [8 empty] | PV7 voltage | [17 empty] | 0.1V
28 |  |  | PV7Curr | [8 empty] | PV7 input current | [17 empty] | 0.1A
29 |  |  | Ppv7 H | [8 empty] | PV7 input power (high) | [17 empty] | 0.1W
30 |  |  | Ppv7 L | [8 empty] | PV7 input power (low) | [17 empty] | 0.1W
31 |  |  | Vpv8 | [8 empty] | PV8 voltage | [17 empty] | 0.1V
32 |  |  | PV8Curr | [8 empty] | PV8 input current | [17 empty] | 0.1A
33 |  |  | Ppv8 H | [8 empty] | PV8 input power (high) | [17 empty] | 0.1W
34 |  |  | Ppv8 L | [8 empty] | PV8 input power (low) | [17 empty] | 0.1W
35 |  |  | Pac H | [8 empty] | Output power (high) | [17 empty] | 0.1W
36 |  |  | Pac L | [8 empty] | Output power (low) | [17 empty] | 0.1W
37 |  |  | Fac | [8 empty] | Grid frequency | [17 empty] | 0.01Hz
38 |  |  | Vac1 | [8 empty] | Three/single phase grid voltage | [17 empty] | 0.1V
39 |  |  | Iac1 | [8 empty] | Three/single phase grid output current | [17 empty] | 0.1A
40 |  |  | Pac1 H | [8 empty] | Three/single phase grid output watt VA (high) | [17 empty] | 0.1VA
41 |  |  | Pac1 L | [8 empty] | Three/single phase grid output watt VA(low) | [17 empty] | 0.1VA
42 |  |  | Vac2 | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V
43 |  |  | Iac2 | [8 empty] | Three phase grid output current | [17 empty] | 0.1A
44 |  |  | Pac2 H | [8 empty] | Three phase grid output power (high) | [17 empty] | 0.1VA
45 |  |  | Pac2 L | [8 empty] | Three phase grid output power (low) | [17 empty] | 0.1VA
46 |  |  | Vac3 | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V
47 |  |  | Iac3 | [8 empty] | Three phase grid output current | [17 empty] | 0.1A
48 |  |  | Pac3 H | [8 empty] | Three phase grid output power (high) | [17 empty] | 0.1VA
49 |  |  | Pac3 L | [8 empty] | Three phase grid output power (low) | [17 empty] | 0.1VA
50 |  |  | Vac_RS | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V |  |  |  |  | Line voltage
51 |  |  | Vac_ST | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V |  |  |  |  | Line voltage
52 |  |  | Vac_TR | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V |  |  |  |  | Line voltage
53 |  |  | Eactoday H | [8 empty] | Today generate energy (high) | [17 empty] | 0.1kWH
54 |  |  | Eac today L | [8 empty] | Today generate energy (low) | [17 empty] | 0.1kWH
55 |  |  | Eac total H | [8 empty] | Total generate energy (high) | [17 empty] | 0.1kWH
56 |  |  | Eac total L | [8 empty] | Total generate energy (low) | [17 empty] | 0.1kWH
57 |  |  | Time total H | [8 empty] | Work time total (high) | [17 empty] | 0.5s
58 |  |  | Time total L | [8 empty] | Work time total (low) | [17 empty] | 0.5s
59 |  |  | Epv1_today H | [8 empty] | PV1Energy today(high) | [17 empty] | 0.1kWh
60 |  |  | Epv1_today L | [8 empty] | PV1Energy today (low) | [17 empty] | 0.1kWh
61 |  |  | Epv1_total H | [8 empty] | PV1Energy total(high) | [17 empty] | 0.1kWh
62 |  |  | Epv1_total L | [8 empty] | PV1Energy total (low) | [17 empty] | 0.1kWh
63 |  |  | Epv2_today H | [8 empty] | PV2Energy today(high) | [17 empty] | 0.1kWh
64 |  |  | Epv2_today L | [8 empty] | PV2Energy today (low) | [17 empty] | 0.1kWh
65 |  |  | Epv2_total H | [8 empty] | PV2Energy total(high) | [17 empty] | 0.1kWh
66 |  |  | Epv2_total L | [8 empty] | PV2Energy total (low) | [17 empty] | 0.1kWh
67 |  |  | Epv3_today H | [8 empty] | PV3 Energy today(high) | [17 empty] | 0.1kWh
68 |  |  | Epv3_today L | [8 empty] | PV3 Energy today (low) | [17 empty] | 0.1kWh
69 |  |  | Epv3_total H | [8 empty] | PV3 Energy total(high) | [17 empty] | 0.1kWh
70 |  |  | Epv3_total L | [8 empty] | PV3 Energy total (low) | [17 empty] | 0.1kWh
71 |  |  | Epv4_today H | [8 empty] | PV4Energy today(high) | [17 empty] | 0.1kWh
72 |  |  | Epv4_today L | [8 empty] | PV4Energy today (low) | [17 empty] | 0.1kWh
73 |  |  | Epv4_total H | [8 empty] | PV4Energy total(high) | [17 empty] | 0.1kWh
74 |  |  | Epv4_total L | [8 empty] | PV4Energy total (low) | [17 empty] | 0.1kWh
75 |  |  | Epv5_today H | [8 empty] | PV5Energy today(high) | [17 empty] | 0.1kWh
76 |  |  | Epv5_today L | [8 empty] | PV5Energy today (low) | [17 empty] | 0.1kWh
77 |  |  | Epv5_total H | [8 empty] | PV5Energy total(high) | [17 empty] | 0.1kWh
78 |  |  | Epv5_total L | [8 empty] | PV5Energy total (low) | [17 empty] | 0.1kWh
79 |  |  | Epv6_today H | [8 empty] | PV6Energy today(high) | [17 empty] | 0.1kWh
80 |  |  | Epv6_today L | [8 empty] | PV6Energy today (low) | [17 empty] | 0.1kWh
81 |  |  | Epv6_total H | [8 empty] | PV6Energy total(high) | [17 empty] | 0.1kWh
82 |  |  | Epv6_total L | [8 empty] | PV6Energy total (low) | [17 empty] | 0.1kWh
83 |  |  | Epv7_today H | [8 empty] | PV7Energy today(high) | [17 empty] | 0.1kWh
84 |  |  | Epv7_today L | [8 empty] | PV7Energy today (low) | [17 empty] | 0.1kWh
85 |  |  | Epv7_total H | [8 empty] | PV7 Energy total(high) | [17 empty] | 0.1kWh
86 |  |  | Epv7_total L | [8 empty] | PV7Energy total (low) | [17 empty] | 0.1kWh
87 |  |  | Epv8_today H | [8 empty] | PV8Energy today(high) | [17 empty] | 0.1kWh
88 |  |  | Epv8_today L | [8 empty] | PV8Energy today (low) | [17 empty] | 0.1kWh
89 |  |  | Epv8_total H | [8 empty] | PV8Energy total(high) | [17 empty] | 0.1kWh
90 |  |  | Epv8_total L | [8 empty] | PV8Energy total (low) | [17 empty] | 0.1kWh
91 |  |  | Epv_total H | [8 empty] | PV Energy total(high) | [17 empty] | 0.1kWh
92 |  |  | Epv_total L | [8 empty] | PV Energy total (low) | [17 empty] | 0.1kWh
93 |  |  | Temp1 | [8 empty] | Inverter temperature | [17 empty] | 0.1C
94 |  |  | Temp2 | [8 empty] | The inside IPM in inverter Temperature | [17 empty] | 0.1C
95 |  |  | Temp3 | [8 empty] | Boost temperature | [17 empty] | 0.1C
96 |  |  | Temp4 | [31 empty] | reserved
97 |  |  | uwBatVolt_DSP | [8 empty] | BatVolt_DSP | [17 empty] | 0.1V |  |  |  |  | BatVolt(DSP)
98 |  |  | P Bus Voltage | [8 empty] | P Bus inside Voltage | [17 empty] | 0.1V
99 |  |  | N Bus Voltage | [8 empty] | N Bus inside Voltage | [17 empty] | 0.1V
100 |  |  | IPF | [8 empty] | Inverter output PF now | [10 empty] | 0-20000
101 |  |  | RealOPPercent | [8 empty] | Real Output power Percent | [17 empty] | 1%
102 |  |  | OPFullwatt H | [8 empty] | Output Maxpower Limited high
103 |  |  | OPFullwatt L | [8 empty] | Output Maxpower Limited low | [17 empty] | 0.1W
104 |  |  | DeratingMode | [8 empty] | DeratingMode | [10 empty] | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime;
105 |  |  | Fault Maincode | [8 empty] | Inverter fault maincode
106
107 |  |  | Fault Subcode | [8 empty] | Inverter fault subcode
108 |  |  | RemoteCtrlEn | [8 empty] | / | [10 empty] | 0.Load First 1.BatFirst 2.Grid | [6 empty] | / |  |  |  |  | StoragePow er (SPA)
109 |  |  | RemoteCtrlPow er | [8 empty] | / | [17 empty] | / |  |  |  |  | StoragePow er (SPA)
110 |  |  | Warning bit H | [8 empty] | Warning bit H
111 |  |  | Warn Subcode | [8 empty] | Inverter warn subcode
112 |  |  | Warn Maincode | [8 empty] | Inverter warn maincode
|  |  | EACharge_Today _H | [8 empty] | ACCharge energy today | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
113 |  |  | real Power Percent | [8 empty] | real Power Percent | [10 empty] | 0-100 | [6 empty] | % |  |  |  |  | MAX
|  |  | EACharge_Today _L | [8 empty] | ACCharge energy today | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
114 |  |  | inv start delay time | [8 empty] | inv start delay time | [22 empty] | MAX
|  |  | EACharge_Total _H | [8 empty] | ACCharge energy total | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
115 |  |  | bINVAllFaultCod e | [8 empty] | bINVAllFaultCode | [22 empty] | MAX
|  |  | EACharge_Total _L | [8 empty] | ACCharge energy total | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
116 |  |  | AC charge Power_H | [8 empty] | Grid power to local load | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
117 |  |  | AC charge Power_L | [8 empty] | Grid power to local load | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
118 |  |  | Priority | [8 empty] | 0:Load First | [22 empty] | Storage
[12 empty] | 1:Battery First 2:Grid First | [22 empty] | Power
119 |  |  | Battery Type | [8 empty] | 0：Lead-acid 1：Lithium battery | [22 empty] | Storage Power
120 |  |  | AutoProofreadC MD | [8 empty] | Aging mode Auto-calibration command | [22 empty] | Storage Power
… |  |  | reserved | [31 empty] | reserved
124 |  |  | reserved | [31 empty] | reserved
Second group
125 |  |  | PID PV1+ Voltage | [9 empty] | PID PV1PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
126 |  |  | PID PV1+ Current | [9 empty] | PID PV1PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
127 |  |  | PID PV2+ Voltage | [9 empty] | PID PV2PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
128 |  |  | PID PV2+ Current | [9 empty] | PID PV2PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
129 |  |  | PID PV3+ Voltage | [9 empty] | PID PV3PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
130 |  |  | PID PV3+ Current | [9 empty] | PID PV3PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
131 |  |  | PID PV4+ Voltage | [9 empty] | PID PV4PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
132 |  |  | PID PV4+ Current | [9 empty] | PID PV4PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
133 |  |  | PID PV5+ Voltage | [9 empty] | PID PV5PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
134 |  |  | PID PV5+ Current | [9 empty] | PID PV5PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
135 |  |  | PID PV6+ Voltage | [9 empty] | PID PV6PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
136 |  |  | PID PV6+ Current | [9 empty] | PID PV6PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
137 |  |  | PID PV7+ Voltage | [9 empty] | PID PV7PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
138 |  |  | PID PV7+ Current | [9 empty] | PID PV7PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
139 |  |  | PID PV8+ Voltage | [9 empty] | PID PV8PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
140 |  |  | PID PV8+ Current | [9 empty] | PID PV8PE Curr | [9 empty] | -10~10mA | [6 empty] | 0.1mA
141 |  |  | PID Status | [9 empty] | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | [9 empty] | 0~3
142 |  |  | V _String1 | [9 empty] | PV String1 voltage | [16 empty] | 0.1V
143 |  |  | Curr _String1 | [9 empty] | PV String1 current | [9 empty] | -15~15A | [6 empty] | 0.1A
144 |  |  | V _String2 | [9 empty] | PV String2 voltage | [16 empty] | 0.1V
145 |  |  | Curr _String2 | [9 empty] | PV String2 current | [9 empty] | -15~15A | [6 empty] | 0.1A
146 |  |  | V _String3 | [9 empty] | PV String3 voltage | [16 empty] | 0.1V
147 |  |  | Curr _String3 | [9 empty] | PV String3 current | [9 empty] | -15~15A | [6 empty] | 0.1A
148 |  |  | V _String4 | [9 empty] | PV String4 voltage | [16 empty] | 0.1V
149 |  |  | Curr _String4 | [9 empty] | PV String4 current | [9 empty] | -15~15A | [6 empty] | 0.1A
150 |  |  | V _String5 | [9 empty] | PV String5 voltage | [16 empty] | 0.1V
151 |  |  | Curr _String5 | [9 empty] | PV String5 current | [9 empty] | -15~15A | [6 empty] | 0.1A
152 |  |  | V _String6 | [9 empty] | PV String6 voltage | [16 empty] | 0.1V
153 |  |  | Curr _String6 | [9 empty] | PV String6 current | [9 empty] | -15~15A | [6 empty] | 0.1A
154 |  |  | V _String7 | [9 empty] | PV String7 voltage | [16 empty] | 0.1V
155 |  |  | Curr _String7 | [9 empty] | PV String7 current | [9 empty] | -15~15A | [6 empty] | 0.1A
156 |  |  | V _String8 | [9 empty] | PV String8 voltage | [16 empty] | 0.1V
157 |  |  | Curr _String8 | [9 empty] | PV String8 current | [9 empty] | -15A~15A | [6 empty] | 0.1A
158 |  |  | V _String9 | [9 empty] | PV String9 voltage | [16 empty] | 0.1V
159 |  |  | Curr _String9 | [9 empty] | PV String9 current | [9 empty] | -15A~15A | [6 empty] | 0.1A
160 |  |  | V _String10 | [9 empty] | PV String10 voltage | [16 empty] | 0.1V
161 |  |  | Curr _String10 | [9 empty] | PV String10 current | [9 empty] | -15~15A | [6 empty] | 0.1A
162 |  |  | V _String11 | [9 empty] | PV String11 voltage | [16 empty] | 0.1V
163 |  |  | Curr _String11 | [9 empty] | PV String11 current | [9 empty] | -15~15A | [6 empty] | 0.1A
164 |  |  | V _String12 | [9 empty] | PV String12 voltage | [16 empty] | 0.1V
165 |  |  | Curr _String12 | [9 empty] | PV String12 current | [9 empty] | -15~15A | [6 empty] | 0.1A
166 |  |  | V _String13 | [9 empty] | PV String13 voltage | [16 empty] | 0.1V
167 |  |  | Curr _String13 | [9 empty] | PV String13 current | [9 empty] | -15A~15A | [6 empty] | 0.1A
168 |  |  | V _String14 | [9 empty] | PV String14 voltage | [16 empty] | 0.1V
169 |  |  | Curr _String14 | [9 empty] | PV String14 current | [9 empty] | -15~15A | [6 empty] | 0.1A
170 |  |  | V _String15 | [9 empty] | PV String15 voltage | [16 empty] | 0.1V
171 |  |  | Curr _String15 | [9 empty] | PV String15 current | [9 empty] | -15~15A | [6 empty] | 0.1A
172 |  |  | V _String16 | [9 empty] | PV String16 voltage | [16 empty] | 0.1V
173 |  |  | Curr _String16 | [9 empty] | PV String16 current | [9 empty] | -15~15A | [6 empty] | 0.1A
174 |  |  | StrUnmatch | [9 empty] | Bit0~15: String1~16 unmatch | [21 empty] | suggestive
175 |  |  | StrCurrentUnblan ce | [9 empty] | Bit0~15: String1~16 current unblance | [21 empty] | suggestive
176 |  |  | StrDisconnect | [9 empty] | Bit0~15: String1~16 disconnect | [21 empty] | suggestive
177 |  |  | PIDFaultCode | [9 empty] | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved
178 |  |  | String Prompt | [9 empty] | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance
Bit3~15:reserved
179 |  |  | PV Warning Value | [9 empty] | PV Warning Value
180 |  |  | DSP075 Warning Value | [9 empty] | DSP075 Warning Value
181 |  |  | DSP075 Fault Value | [9 empty] | DSP075 Fault Value
182 |  |  | DSP067 Debug Data1 | [9 empty] | DSP067 Debug Data1
183 |  |  | DSP067 Debug Data2 | [9 empty] | DSP067 Debug Data2
184 |  |  | DSP067 Debug Data3 | [9 empty] | DSP067 Debug Data3
185 |  |  | DSP067 Debug Data4 | [9 empty] | DSP067 Debug Data4
186 |  |  | DSP067 Debug Data5 | [9 empty] | DSP067 Debug Data5
187 |  |  | DSP067 Debug Data6 | [9 empty] | DSP067 Debug Data6
188 |  |  | DSP067 Debug Data7 | [9 empty] | DSP067 Debug Data7
189 |  |  | DSP067 Debug Data8 | [9 empty] | DSP067 Debug Data8
190 |  |  | DSP075 Debug Data1 | [9 empty] | DSP075 Debug Data1
191 |  |  | DSP075 Debug Data2 | [9 empty] | DSP075 Debug Data2
192 |  |  | DSP075 Debug Data3 | [9 empty] | DSP075 Debug Data3
193 |  |  | DSP075 Debug Data4 | [9 empty] | DSP075 Debug Data4
194 |  |  | DSP075 Debug Data55 | [9 empty] | DSP075 Debug Data5
195 |  |  | DSP075 Debug Data6 | [9 empty] | DSP075 Debug Data6
196 |  |  | DSP075 Debug Data7 | [9 empty] | DSP075 Debug Data7
197 |  |  | DSP075 Debug Data8 | [9 empty] | DSP075 Debug Data8
198 |  |  | bUSBAgingTestOk Flag | [9 empty] | USBAgingTestOkFlag | [9 empty] | 0-1
199 |  |  | bFlashEraseAging OkFlag | [9 empty] | FlashEraseAgingOkFlag | [9 empty] | 0-1
200 |  |  | PVISO | [9 empty] | PVISOValue | [16 empty] | KΩ
201 |  |  | R_DCI | [9 empty] | R DCI Curr | [16 empty] | 0.1mA
202 |  |  | S_DCI | [9 empty] | S DCI Curr | [16 empty] | 0.1mA
203 |  |  | T_DCI | [9 empty] | T DCI Curr | [16 empty] | 0.1mA
204 |  |  | PID_Bus | [9 empty] | PIDBusVolt | [16 empty] | 0.1V
205 |  |  | GFCI | [9 empty] | GFCI Curr | [16 empty] | mA
206 |  |  | SVG/APF Status+SVGAPFEq ualRatio | [9 empty] | SVG/APF Status+SVGAPFEqualRatio | [9 empty] | High 8 bit： SVGAPFEqua lRatio Low 8 bit： SVG/APF Status 0:None 1:SVG Run 2:APF Run 3:SVG/APF Run
207 |  |  | CT_I _R | [9 empty] | R phase load side current for SVG | [16 empty] | 0.1A
208 |  |  | CT_I _S | [9 empty] | S phase load side current for SVG | [16 empty] | 0.1A
209 |  |  | CT_I _T | [9 empty] | T phase load side current for SVG | [16 empty] | 0.1A
210 |  |  | CT_Q _R H | [9 empty] | R phase load side output reactive power for SVG(High) | [16 empty] | 0.1Var
211 |  |  | CT_Q _R L | [9 empty] | R phase load side output reactive power for SVG(low) | [16 empty] | 0.1Var
212 |  |  | CT_Q _S H | [9 empty] | S phase load side output reactive power for SVG(High) | [16 empty] | 0.1Var
213 |  |  | CT_Q _S L | [9 empty] | S phase load side output reactive power for SVG(low) | [16 empty] | 0.1Var
214 |  |  | CT_Q _T H | [9 empty] | T phase load side output reactive power for SVG(High) | [16 empty] | 0.1Var
215 |  |  | CT_Q _T L | [9 empty] | T phase load side output reactive power for SVG(low) | [16 empty] | 0.1Var
216 |  |  | CT HAR_I_R | [9 empty] | R phase load side harmonic | [16 empty] | 0.1A
217 |  |  | CT HAR_I_S | [9 empty] | S phase load side harmonic | [16 empty] | 0.1A
218 |  |  | CT HAR_I_T | [9 empty] | T phase load side harmonic | [16 empty] | 0.1A
219 |  |  | COMP_Q _R H | [9 empty] | R phase compensate reactive power for SVG(High) | [16 empty] | 0.1Var
220 |  |  | COMP_Q _R L | [9 empty] | R phase compensate reactive power for SVG(low) | [16 empty] | 0.1Var
221 |  |  | COMP_Q _S H | [9 empty] | S phase compensate reactive power for SVG(High) | [16 empty] | 0.1Var
222 |  |  | COMP_Q _S L | [9 empty] | S phase compensate reactive power | [16 empty] | 0.1Var
for SVG(low)
223 |  |  | COMP_Q _T H | [9 empty] | T phase compensate reactive power for SVG(High) | [16 empty] | 0.1Var
224 |  |  | COMP_Q _T L | [9 empty] | T phase compensate reactive power for SVG(low) | [16 empty] | 0.1Var
225 |  |  | COMP HAR_I_R | [9 empty] | R phase compensate harmonic for SVG | [16 empty] | 0.1A
226 |  |  | COMP HAR_I_S | [9 empty] | S phase compensate harmonic for SVG | [16 empty] | 0.1A
227 |  |  | COMP HAR_I_T | [9 empty] | T phase compensate harmonic for SVG | [16 empty] | 0.1A
228 |  |  | bRS232AgingTest OkFlag | [9 empty] | RS232AgingTestOkFlag | [9 empty] | 0-1
229 |  |  | bFanFaultBit | [9 empty] | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit Bit2: Fan 3 fault bit Bit3: Fan 4 fault bit Bit4-7: Reserved
230 |  |  | Sac H | [9 empty] | Output apparent power H | [16 empty] | 0.1W
231 |  |  | Sac L | [9 empty] | Output apparent power L | [16 empty] | 0.1W
232 |  |  | ReActPowerH | [9 empty] | Real Output Reactive Power H | [9 empty] | Int32 | [6 empty] | 0.1W
233 |  |  | ReActPowerL | [9 empty] | Real Output Reactive Power L
234 |  |  | ReActPowerMaxH | [9 empty] | Nominal Output Reactive Power H | [16 empty] | 0.1var
235 |  |  | ReActPowerMaxL | [9 empty] | Nominal Output Reactive Power L
236 |  |  | ReActPower_Total H | [9 empty] | Reactive power generation | [16 empty] | 0.1kwh
237 |  |  | ReActPower_Total L | [9 empty] | Reactive power generation
238 |  |  | bAfciStatus | [9 empty] | 0：Waiting 1：Self-check state 2：Detect pull arc state 3：Fault 4：Update
239 |  |  | uwPresentFFTValu e [CHANNEL_A] | [9 empty] | PresentFFTValue [CHANNEL_A]
240 |  |  | uwPresentFFTValu e [CHANNEL_B] | [9 empty] | PresentFFTValue [CHANNEL_B]
241 |  |  | DSP067 Debug Data1 | [9 empty] | DSP067 Debug Data1
242 |  |  | DSP067 Debug Data2 | [9 empty] | DSP067 Debug Data2
243 |  |  | DSP067 Debug | [9 empty] | DSP067 Debug Data3
Data3
244 |  |  | DSP067 Debug Data4 | [9 empty] | DSP067 Debug Data4
245 |  |  | DSP067 Debug Data5 | [9 empty] | DSP067 Debug Data5
246 |  |  | DSP067 Debug Data6 | [9 empty] | DSP067 Debug Data6
247 |  |  | DSP067 Debug Data7 | [9 empty] | DSP067 Debug Data7
248 |  |  | DSP067 Debug Data8 | [9 empty] | DSP067 Debug Data8
249 | [34 empty] | reserved
The eighth group for PV9-PV16 information
875 |  |  | Vpv9 | [9 empty] | PV9 voltage | [16 empty] | 0.1V
876 |  |  | PV9Curr | [9 empty] | PV9 Input current | [16 empty] | 0.1A
877 |  |  | Ppv9 H | [9 empty] | PV9 input power (High) | [16 empty] | 0.1W
878 |  |  | Ppv9 L | [9 empty] | PV9 input power (Low) | [16 empty] | 0.1W
879 |  |  | Vpv10 | [9 empty] | PV10 voltage | [16 empty] | 0.1V
880 |  |  | PV10Curr | [9 empty] | PV10 Input current | [16 empty] | 0.1A
881 |  |  | Ppv10 H | [9 empty] | PV10 input power (High) | [16 empty] | 0.1W
882 |  |  | Ppv10 L | [9 empty] | PV10 input power (Low) | [16 empty] | 0.1W
883 |  |  | Vpv11 | [9 empty] | PV11 voltage | [16 empty] | 0.1V
884 |  |  | PV11Curr | [9 empty] | PV11 Input current | [16 empty] | 0.1A
885 |  |  | Ppv11 H | [9 empty] | PV11 input power (High) | [16 empty] | 0.1W
886 |  |  | Ppv11 L | [9 empty] | PV11 input power (Low) | [16 empty] | 0.1W
887 |  |  | Vpv12 | [9 empty] | PV12 voltage | [16 empty] | 0.1V
888 |  |  | PV12Curr | [9 empty] | PV12 Input current | [16 empty] | 0.1A
889 |  |  | Ppv12 H | [9 empty] | PV12 input power (High) | [16 empty] | 0.1W
890 |  |  | Ppv12 L | [9 empty] | PV12 input power (Low) | [16 empty] | 0.1W
891 |  |  | Vpv13 | [9 empty] | PV13 voltage | [16 empty] | 0.1V
892 |  |  | PV13Curr | [9 empty] | PV13 Input current | [16 empty] | 0.1A
893 |  |  | Ppv13H | [9 empty] | PV13 input power (High) | [16 empty] | 0.1W
894 |  |  | Ppv13 L | [9 empty] | PV13 input power (Low) | [16 empty] | 0.1W
895 |  |  | Vpv14 | [9 empty] | PV14 voltage | [16 empty] | 0.1V
896 |  |  | PV14Curr | [9 empty] | PV14 Input current | [16 empty] | 0.1A
897 |  |  | Ppv14 H | [9 empty] | PV14 input power (High) | [16 empty] | 0.1W
898 |  |  | Ppv14 L | [9 empty] | PV14 input power (Low) | [16 empty] | 0.1W
899 |  |  | Vpv15 | [9 empty] | PV15 voltage | [16 empty] | 0.1V
900 |  |  | PV15Curr | [9 empty] | PV15 Input current | [16 empty] | 0.1A
901 |  |  | Ppv15 H | [9 empty] | PV15 input power (High) | [16 empty] | 0.1W
902 |  |  | Ppv15 L | [9 empty] | PV15 input power (Low) | [16 empty] | 0.1W
903 |  |  | Vpv16 | [9 empty] | PV16 voltage | [16 empty] | 0.1V
904 |  |  | PV16Curr | [9 empty] | PV16 Input current | [16 empty] | 0.1A
905 |  |  | Ppv16 H | [9 empty] | PV16 input power (High) | [16 empty] | 0.1W
906 |  |  | Ppv16 L | [9 empty] | PV16 input power (Low) | [16 empty] | 0.1W
907 |  |  | Epv9_today H | [9 empty] | PV9 energy today (High) | [16 empty] | 0.1kWh
908 |  |  | Epv9_today L | [9 empty] | PV9 energy today (Low) | [16 empty] | 0.1kWh
909 |  |  | Epv9_total H | [9 empty] | PV9 energy total (High) | [16 empty] | 0.1kWh
910 |  |  | Epv9_total L | [9 empty] | PV9 energy total (Low) | [16 empty] | 0.1kWh
911 |  |  | Epv10_today H | [9 empty] | PV10 energy today (High) | [16 empty] | 0.1kWh
912 |  |  | Epv10_today L | [9 empty] | PV10 energy today (Low) | [16 empty] | 0.1kWh
913 |  |  | Epv10_total H | [9 empty] | PV10 energy total (High) | [16 empty] | 0.1kWh
914 |  |  | Epv10_total L | [9 empty] | PV10 energy total (Low) | [16 empty] | 0.1kWh
915 |  |  | Epv11_today H | [9 empty] | PV11 energy today (High) | [16 empty] | 0.1kWh
916 |  |  | Epv11_today L | [9 empty] | PV11 energy today (Low) | [16 empty] | 0.1kWh
917 |  |  | Epv11_total H | [9 empty] | PV11 energy total (High) | [16 empty] | 0.1kWh
918 |  |  | Epv11_total L | [9 empty] | PV11 energy total (Low) | [16 empty] | 0.1kWh
919 |  |  | Epv12_today H | [9 empty] | PV12 energy today (High) | [16 empty] | 0.1kWh
920 |  |  | Epv12_today L | [9 empty] | PV12 energy today (Low) | [16 empty] | 0.1kWh
921 |  |  | Epv12_total H | [9 empty] | PV12 energy total (High) | [16 empty] | 0.1kWh
922 |  |  | Epv12_total L | [9 empty] | PV12 energy total (Low) | [16 empty] | 0.1kWh
923 |  |  | Epv13_today H | [9 empty] | PV13 energy today (High) | [16 empty] | 0.1kWh
924 |  |  | Epv13_today L | [9 empty] | PV13 energy today (Low) | [16 empty] | 0.1kWh
925 |  |  | Epv13_total H | [9 empty] | PV13 energy total (High) | [16 empty] | 0.1kWh
926 |  |  | Epv13_total L | [9 empty] | PV13 energy total (Low) | [16 empty] | 0.1kWh
927 |  |  | Epv14_today H | [9 empty] | PV14 energy today (High) | [16 empty] | 0.1kWh
928 |  |  | Epv14_today L | [9 empty] | PV14 energy today (Low) | [16 empty] | 0.1kWh
929 |  |  | Epv14_total H | [9 empty] | PV14 energy total (High) | [16 empty] | 0.1kWh
930 |  |  | Epv14_total L | [9 empty] | PV14 energy total (Low) | [16 empty] | 0.1kWh
931 |  |  | Epv15_today H | [9 empty] | PV15 energy today (High) | [16 empty] | 0.1kWh
932 |  |  | Epv15_today L | [9 empty] | PV15 energy today (Low) | [16 empty] | 0.1kWh
933 |  |  | Epv15_total H | [9 empty] | PV15 energy total (High) | [16 empty] | 0.1kWh
934 |  |  | Epv15_total L | [9 empty] | PV15 energy total (Low) | [16 empty] | 0.1kWh
935 |  |  | Epv16_today H | [9 empty] | PV16 energy today (High) | [16 empty] | 0.1kWh
936 |  |  | Epv16_today L | [9 empty] | PV16 energy today (Low) | [16 empty] | 0.1kWh
937 |  |  | Epv16_total H | [9 empty] | PV16 energy total (High) | [16 empty] | 0.1kWh
938 |  |  | Epv16_total L | [9 empty] | PV16 energy total (Low) | [16 empty] | 0.1kWh
939 |  |  | PID PV9+ Voltage | [9 empty] | PID PV9PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
940 |  |  | PID PV9+ Current | [9 empty] | PID PV9PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
941 |  |  | PID PV10+ Voltage | [9 empty] | PID PV10PE/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
942 |  |  | PID PV10+ Current | [9 empty] | PID PV10PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
943 |  |  | PID PV11+ Voltage | [9 empty] | PID PV11PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
944 |  |  | PID PV11+ Current | [9 empty] | PID PV11PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
945 |  |  | PID PV12+ Voltage | [9 empty] | PID PV12PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
946 |  |  | PID PV12+ Current | [9 empty] | PID PV12PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
947 |  |  | PID PV13+ Voltage | [9 empty] | PID PV13PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
948 |  |  | PID PV13+ Current | [9 empty] | PID PV13PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
949 |  |  | PID PV14+ Voltage | [9 empty] | PID PV14PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
950 |  |  | PID PV14+ Current | [9 empty] | PID PV14PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
951 |  |  | PID PV15+ Voltage | [9 empty] | PID PV15PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
952 |  |  | PID PV15+ Current | [9 empty] | PID PV15PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
953 |  |  | PID PV16+ Voltage | [9 empty] | PID PV16PE Volt/ Flyspan voltage (MAX HV) | [9 empty] | 0~1000V | [6 empty] | 0.1V
954 |  |  | PID PV16+ Current | [9 empty] | PID PV16PE Current | [9 empty] | -10~10mA | [6 empty] | 0.1mA
955 |  |  | V _String17 | [9 empty] | PV String 17 voltage | [16 empty] | 0.1V
956 |  |  | Curr _String17 | [9 empty] | PV String 17 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
957 |  |  | V _String18 | [9 empty] | PV String 18 voltage | [16 empty] | 0.1V
958 |  |  | Curr _String18 | [9 empty] | PV String 18 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
959 |  |  | V _String19 | [9 empty] | PV String 19 voltage | [16 empty] | 0.1V
960 |  |  | Curr _String19 | [9 empty] | PV String 19 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
961 |  |  | V _String20 | [9 empty] | PV String 20 voltage | [16 empty] | 0.1V
962 |  |  | Curr _String20 | [9 empty] | PV String 20 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
963 |  |  | V _String21 | [9 empty] | PV String 21 voltage | [16 empty] | 0.1V
964 |  |  | Curr _String21 | [9 empty] | PV String 21 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
965 |  |  | V _String22 | [9 empty] | PV String22 voltage | [16 empty] | 0.1V
966 |  |  | Curr _String22 | [9 empty] | PV String 22 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
967 |  |  | V _String23 | [9 empty] | PV String 23 voltage | [16 empty] | 0.1V
968 |  |  | Curr _String23 | [9 empty] | PV String 23 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
969 |  |  | V _String24 | [9 empty] | PV String 24 voltage | [16 empty] | 0.1V
970 |  |  | Curr _String24 | [9 empty] | PV String 24 Current | [9 empty] | -15A~15A | [6 empty] | 0.1A
971 |  |  | V _String25 | [9 empty] | PV String 25 voltage | [16 empty] | 0.1V
972 |  |  | Curr _String25 | [9 empty] | PV String 25 Current | [9 empty] | -15A~15A | [6 empty] | 0.1A
973 |  |  | V _String26 | [9 empty] | PV String 26 voltage | [16 empty] | 0.1V
974 |  |  | Curr _String26 | [9 empty] | PV String 26 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
975 |  |  | V _String27 | [9 empty] | PV String 27 voltage | [16 empty] | 0.1V
976 |  |  | Curr _String27 | [9 empty] | PV String 27 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
977 |  |  | V _String28 | [9 empty] | PV String 28 voltage | [16 empty] | 0.1V
978 |  |  | Curr _String28 | [9 empty] | PV String 28 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
979 |  |  | V _String29 | [9 empty] | PV String 29 voltage | [16 empty] | 0.1V
980 |  |  | Curr _String29 | [9 empty] | PV String 29 Current | [9 empty] | -15A~15A | [6 empty] | 0.1A
981 |  |  | V _String30 | [9 empty] | PV String 30 voltage | [16 empty] | 0.1V
982 |  |  | Curr _String30 | [9 empty] | PV String 30 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
983 |  |  | V _String31 | [9 empty] | PV String 31 voltage | [16 empty] | 0.1V
984 |  |  | Curr _String31 | [9 empty] | PV String 31 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
985 |  |  | V _String32 | [9 empty] | PV String 32 voltage | [16 empty] | 0.1V
986 |  |  | Curr _String32 | [9 empty] | PV String 32 Current | [9 empty] | -15~15A | [6 empty] | 0.1A
987 |  |  | StrUnmatch2 | [9 empty] | Bit0~15: String 17~32 unmatch
988 |  |  | StrCurrentUnblan ce2 | [9 empty] | Bit0~15:String 17~32 current unblance
989 |  |  | StrDisconnect2 | [9 empty] | Bit0~15: String 17~32 disconnect
990 |  |  | PV Warning Value | [9 empty] | PV Warning Value (PV9-PV16) Contains PV9~16 abnormal ， 和 Boost9~16 Drive anomalies
991 |  |  | StrWaringvalue1 | [9 empty] | string1~string16 abnormal
992 |  |  | StrWaringvalue2 | [9 empty] | string17~string32 abnormal
……
999 |  |  | SystemCmd | [9 empty] | M3 to DSP system command | [21 empty] | system command
Ninth group for Storage power
1000 |  |  | uwSysWorkMode | [10 empty] | System work mode | [7 empty] | 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03：SysFault module 0x04: Flash module | [10 empty] | Theworkingmode displayed by the monitoring to the customer is： 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash
[22 empty] | 0x05 ： PVBATOnline module, 0x06 ： BatOnline module, 0x07 ： PVOfflineMod e module, 0x08 ： BatOfflineMo de module, | [10 empty] | module 0x05¦0x06¦0x07¦0 x08:normal module
1001 |  |  | Systemfault word0 | [10 empty] | System fault word0 | [18 empty] | Please refer thefault description Hybrid |  |  |  |  | to of
1002 |  |  | Systemfault word1 | [10 empty] | System fault word1
1003 |  |  | Systemfault word2 | [10 empty] | System fault word2
1004 |  |  | Systemfault word3 | [10 empty] | System fault word3
1005 |  |  | Systemfault word4 | [10 empty] | System fault word4
1006 |  |  | Systemfault word5 | [10 empty] | System fault word5
1007 |  |  | Systemfault word6 | [10 empty] | System fault word6
1008 |  |  | Systemfault word7 | [10 empty] | System fault word7
1009 |  |  | Pdischarge1 H | [10 empty] | Discharge power(high) | [14 empty] | 0.1W
1010 |  |  | Pdischarge1 L | [10 empty] | Discharge power (low) | [14 empty] | 0.1W
1011 |  |  | Pcharge1 H | [10 empty] | Charge power(high) | [14 empty] | 0.1W
1012 |  |  | Pcharge1 L | [10 empty] | Charge power (low) | [14 empty] | 0.1W
1013 |  |  | Vbat | [10 empty] | Battery voltage | [14 empty] | 0.1V
1014 |  |  | SOC | [10 empty] | State of charge Capacity | [7 empty] | 0-100 | [6 empty] | 1% |  |  |  | lith/leadacid
1015 |  |  | Pactouser R | [6 empty] | H |  |  |  | AC power to user H | [14 empty] | 0.1w
1016 |  |  | Pactouser R | [6 empty] | L |  |  |  | AC power to user L | [14 empty] | 0.1w
1017 |  |  | Pactouser S | [6 empty] | H |  |  |  | Pactouser S |  |  | H | [11 empty] | 0.1w
1018 |  |  | Pactouser S | [6 empty] | L |  |  |  | Pactouser S |  |  | L | [11 empty] | 0.1w
1019 |  |  | Pactouser T | [6 empty] | H |  |  |  | Pactouser T |  |  | H | [11 empty] | 0.1w
1020 |  |  | Pactouser T | [6 empty] | L |  |  |  | Pactouser T |  |  | H | [11 empty] | 0.1w
1021 |  |  | PactouserTotal H | [10 empty] | AC power to user total H | [14 empty] | 0.1w
1022 |  |  | PactouserTotal L | [10 empty] | AC power to user total L | [14 empty] | 0.1w
1023 |  |  | Pac to grid R | [6 empty] | H |  |  |  | AC power to grid H | [14 empty] | 0.1w |  |  |  | Ac output
1024 |  |  | Pac to grid R | [6 empty] | L |  |  |  | AC power to grid L | [14 empty] | 0.1w
1025 |  |  | Pactogrid S | [6 empty] | H | [18 empty] | 0.1w
1026 |  |  | Pactogrid S | [6 empty] | L | [18 empty] | 0.1w
1027 |  |  | Pactogrid T H | [24 empty] | 0.1w
1028 |  |  | Pactogrid T L | [24 empty] | 0.1w
1029 |  |  | Pactogrid total H | [10 empty] | AC power to grid total H | [13 empty] | 0.1w
1030 |  |  | Pactogrid total L | [10 empty] | AC power to grid total L | [13 empty] | 0.1w
1031 |  |  | PLocalLoad R H | [10 empty] | INV power to local load H | [13 empty] | 0.1w
1032 |  |  | PLocalLoad R L | [10 empty] | INV power to local load L | [13 empty] | 0.1w
1033 |  |  | PLocalLoad S H | [24 empty] | 0.1w
1034 |  |  | PLocalLoad S L | [24 empty] | 0.1w
1035 |  |  | PLocalLoadT H | [24 empty] | 0.1w
1036 |  |  | PLocalLoadT L | [24 empty] | 0.1w
1037 |  |  | PLocalLoad total H | [10 empty] | INV power to local load total H | [13 empty] | 0.1w
1038 |  |  | PLocalLoad total L | [10 empty] | INV power to local load total L | [13 empty] | 0.1w
1039 |  |  | IPM Temperature | [10 empty] | REC Temperature | [13 empty] | 0.1℃ |  |  |  |  | No use
1040 |  |  | Battery Temperature | [10 empty] | Battery Temperature | [13 empty] | 0.1℃ |  |  |  |  | Lead acid/lithium battery temp
1041 |  |  | SP DSP Status | [10 empty] | SP state | [18 empty] | CHG/DisCHG
1042 |  |  | SP Bus Volt | [10 empty] | SP BUS2 Volt | [13 empty] | 0.1V
1043
Power generation data
1044 |  | Etouser_today H | [9 empty] | Energy to user today high | [15 empty] | 0.1kWh
1045 |  | Etouser_today L | [9 empty] | Energy to user today low | [15 empty] | 0.1kWh
1046 |  | Etouser_total H | [9 empty] | Energy to user total high | [15 empty] | 0.1kWh
1047 |  | Etouser_ total L | [9 empty] | Energy to user total high | [15 empty] | 0.1kWh
1048 |  | Etogrid_today H | [9 empty] | Energy to grid today high | [15 empty] | 0.1kWh
1049 |  | Etogrid _today L | [9 empty] | Energy to grid today low | [15 empty] | 0.1kWh
1050 |  | Etogrid _total H | [9 empty] | Energy to grid total high | [15 empty] | 0.1kWh
1051 |  | Etogrid _ total L | [9 empty] | Energy to grid total high | [15 empty] | 0.1kWh
1052 |  | Edischarge1_toda y H | [9 empty] | Discharge energy1 today | [15 empty] | 0.1kWh
1053 |  | Edischarge1_toda y L | [9 empty] | Discharge energy1 today | [15 empty] | 0.1kWh
1054 |  | Edischarge1_total H | [9 empty] | Total discharge energy1 (high) | [15 empty] | 0.1kWh
1055 |  | Edischarge1_total L | [9 empty] | Total discharge energy1 (low) | [15 empty] | 0.1kWh
1056 |  | Echarge1_today H | [9 empty] | Charge1 energy today | [15 empty] | 0.1kWh
1057 |  | Echarge1_today L | [9 empty] | Charge1 energy today | [15 empty] | 0.1kWh
1058 |  | Echarge1_total H | [9 empty] | Charge1 energy total | [15 empty] | 0.1kWh
1059 |  | Echarge1_total L | [9 empty] | Charge1 energy total | [15 empty] | 0.1kWh
1060 |  | ELocalLoad_Today H | [9 empty] | Local load energy today | [15 empty] | 0.1kWh
1061 |  | ELocalLoad_Today L | [9 empty] | Local load energy today | [15 empty] | 0.1kWh
1062 |  | ELocalLoad_Total H | [9 empty] | Local load energy total | [15 empty] | 0.1kWh
1063 |  | ELocalLoad_Total L | [9 empty] | Local load energy total | [15 empty] | 0.1kWh
1064 |  | dwExportLimitAp parentPower | [9 empty] | ExportLimitApparentPower H | [15 empty] | 0.1kWh |  |  |  |  | ApparentPower
1065 |  | dwExportLimitAp parentPower | [9 empty] | ExportLimitApparentPower L | [15 empty] | 0.1kWh |  |  |  |  | ApparentPower
1066 |  | / | [9 empty] | / | [9 empty] | / | [5 empty] | / |  |  |  |  | reserved
Ups information (offline)
1067 |  | EPS Fac | [9 empty] | UPSfrequency | [9 empty] | 5000/6000 | [5 empty] | 0.01Hz
1068 |  | EPS Vac1 | [9 empty] | UPS phase R output voltage | [9 empty] | 2300 | [5 empty] | 0.1V
1069 |  | EPS Iac1 | [9 empty] | UPS phase R output current | [15 empty] | 0.1A
1070 |  | EPS Pac1 H | [9 empty] | UPS phase R output power (H) | [15 empty] | 0.1VA
1071 |  | EPS Pac1 L | [9 empty] | UPS phase R output power (L) | [15 empty] | 0.1VA
1072 |  | EPS Vac2 | [9 empty] | UPS phase S output voltage | [15 empty] | 0.1V
1073 |  | EPS Iac2 | [9 empty] | UPS phase S output current | [15 empty] | 0.1A |  |  |  |  | No use
1074 |  | EPS Pac2 H | [9 empty] | UPS phase S output power (H) | [15 empty] | 0.1VA
1075 |  | EPS Pac2 L | [9 empty] | UPS phase S output power (L) | [15 empty] | 0.1VA
1076 |  | EPS Vac3 | [9 empty] | UPS phase T output voltage | [15 empty] | 0.1V
1077 |  | EPS Iac3 | [9 empty] | UPS phase T output current | [15 empty] | 0.1A |  |  |  |  | No use
1078 |  | EPS Pac3 H | [9 empty] | UPS phase T output power (H) | [15 empty] | 0.1VA
1079 |  | EPS Pac3 L | [9 empty] | UPS phase T output power (L) | [15 empty] | 0.1VA
1080 |  | Loadpercent | [9 empty] | Load percent of UPS ouput | [9 empty] | 0-100 | [5 empty] | 1%
1081 |  | PF | [9 empty] | Power factor | [9 empty] | 0-2 | [5 empty] | 0.1 |  |  |  |  | Primary Value+1
BMS Infomation
1082 |  |  | BMS_StatusOld | [8 empty] | StatusOld from BMS | [9 empty] | Detail information, refer to document:GrowattxxSxx P ESS Protocol;
1083 |  |  | BMS_Status | [8 empty] | Status from BMS | [20 empty] | W/R
1084 |  |  | BMS_ErrorOld | [8 empty] | Error info Old from BMS
1085 |  |  | BMS_Error | [8 empty] | Errorinfomation from BMS
1086 |  |  | BMS_SOC | [8 empty] | SOC from BMS | [20 empty] | R SPH6K
1087 |  |  | BMS_BatteryVol t | [8 empty] | Battery voltage from BMS | [20 empty] | R SPH6K
1088 |  |  | BMS_BatteryCur r | [8 empty] | Battery current from BMS
1089 |  |  | BMS_BatteryTe mp | [8 empty] | Battery temperature from BMS
1090 |  |  | BMS_MaxCurr | [8 empty] | Max. charge/discharge current from BMS (pylon)
1091 |  |  | BMS_GaugeRM | [8 empty] | Gauge RM from BMS
1092 |  |  | BMS_GaugeFCC | [8 empty] | Gauge FCC from BMS
1093 |  |  | BMS_FW
1094 |  |  | BMS_DeltaVolt | [8 empty] | Delta V from BMS
1095 |  |  | BMS_CycleCnt | [8 empty] | Cycle Count from BMS
1096 |  |  | BMS_SOH | [8 empty] | SOH from BMS
1097 |  |  | BMS_ConstantV olt | [8 empty] | CV voltage from BMS
1098 |  |  | BMS_WarnInfoO ld | [8 empty] | Warning info old from BMS
1099 |  |  | BMS_WarnInfo | [8 empty] | Warning info from BMS
1100 |  |  | BMS_GaugeICCu rr | [8 empty] | Gauge IC current from BMS
1101 |  |  | BMS_MCUVersi on | [8 empty] | MCU Software version from BMS
1102 |  |  | BMS_GaugeVers ion | [8 empty] | Gauge Version from BMS
1103 |  |  | BMS_wGaugeFR Version_ L | [8 empty] | Gauge FR Version L16 from BMS
1104 |  |  | BMS_wGaugeFR Version_H | [8 empty] | Gauge FR Version H16 from BMS
1105 |  |  | BMS_BMSInfo | [8 empty] | BMSInformation from BMS
1106 |  |  | BMS_PackInfo | [8 empty] | Pack Information from BMS
1107 |  |  | BMS_UsingCap | [8 empty] | Using Cap from BMS
1108 |  |  | uwMaxCellVolt | [8 empty] | Maximum single battery voltage | [14 empty] | 0.001V
1109 |  |  | uwMinCellVolt | [8 empty] | Lowest single battery voltage | [14 empty] | 0.001V
1110 |  |  | bModuleNum | [8 empty] | Battery parallel number | [14 empty] | 1
1111 | [11 empty] | Number of batteries | [14 empty] | 1
1112 |  |  | uwMaxVoltCellN o | [8 empty] | MaxVoltCellNo | [14 empty] | 1
1113 |  |  | uwMinVoltCellN o | [8 empty] | MinVoltCellNo | [14 empty] | 1
1114 |  |  | uwMaxTemprCe ll_10T | [8 empty] | MaxTemprCell_10T | [14 empty] | 0.1℃
1115 |  |  | uwMinTemprCel l_10T | [8 empty] | MinTemprCell_10T | [14 empty] | 0.1℃
1116 |  |  | uwMaxTemprCe llNo | [8 empty] | MaxVoltTemprCellNo | [14 empty] | 1
1117 |  |  | uwMinTemprCel | [8 empty] | MinVoltTemprCellNo | [14 empty] | 1
lNo
1118 |  |  | Protect pack ID | [8 empty] | Faulty Battery Address | [14 empty] | 1
1119 |  |  | MaxSOC | [8 empty] | Parallel maximum SOC | [14 empty] | 1%
1120 |  |  | MinSOC | [8 empty] | Parallel minimum SOC | [14 empty] | 1%
1121 |  |  | BMS_Error2 | [8 empty] | Battery Protection 2 | [14 empty] | - | [5 empty] | CAN ID ： 0x323 Byte4~5
1122 |  |  | BMS_Error3 | [8 empty] | Battery Protection3 | [14 empty] | - | [5 empty] | CAN ID ： 0x323 Byte6
1123 |  |  | BMS_WarnInfo2 | [8 empty] | Battery Warn2 | [14 empty] | - | [5 empty] | CAN ID ： 0x323 Byte7
1124 |  |  | AC Charge Energy Today H | [8 empty] | AC Charge Energy today | [9 empty] | kwh | [10 empty] | Energy today
Ninth group reserved for storage power
1125 |  |  | ACCharge Energy TodayL | [8 empty] | AC Charge Energy today | [9 empty] | kwh
1126 |  |  | AC Charge Energy Total H | [29 empty] | Energy total
1127 |  |  | ACCharge Energy Total L
1128 |  |  | AC Power |  |  |  | Charge H |  |  |  |  | AC Charge Power | [9 empty] | W
1129 |  |  | AC Power L |  |  |  | Charge |  |  |  |  | AC Charge Power | [9 empty] | w
1130 |  |  | 70% INV Power adjust | [8 empty] | uwGridPower_70_AdjEE_SP | [9 empty] | W
1131 |  |  | Extra AC Power to grid_H | [8 empty] | Extra inverte AC Power to grid High | [9 empty] | For SPA connect inverter | [10 empty] | SPA used
1132 |  |  | Extra AC Power to grid_L | [8 empty] | Extrainverte AC Power to grid Low | [20 empty] | SPA used
1133 |  |  | Eextra_today H | [8 empty] | Extra inverter PowerTOUser_Extra today (high) | [9 empty] | R | [5 empty] | 0.1kWh |  |  |  |  | SPA |  |  | used
1134 |  |  | Eextra_today L | [8 empty] | Extra inverter PowerTOUser_Extra today (low) | [9 empty] | R | [5 empty] | 0.1kWh |  |  |  |  | SPA |  |  | used
1135 |  |  | Eextra_total H | [8 empty] | Extra inverter PowerTOUser_Extra total(high) | [15 empty] | 0.1kWh |  |  |  |  | SPA |  |  | used
1136 |  |  | Eextra_total L | [8 empty] | Extra inverter PowerTOUser_Extra total(low) | [15 empty] | 0.1kWh |  |  |  |  | SPA |  |  | used
1137 |  |  | Esystem_today H | [8 empty] | System electric energy today H | [15 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today H
1138 |  |  | Esystem_ L |  |  |  |  | today |  |  |  | System electric energy today L | [15 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today L
1139 |  |  | Esystem_total H | [8 empty] | System electric energy total H | [15 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy total H
1140 |  |  | Esystem_ total L | [8 empty] | System electric energy total L | [15 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy total L
1141 |  |  | Eself_today H | [8 empty] | self electric energy today H | [15 empty] | 0.1kWh |  |  |  |  | self electric energy today H
1142 |  |  | Eself_ today L | [8 empty] | self electric energy today L | [15 empty] | 0.1kWh |  |  |  |  | self electric energy today L
1143 |  |  | Eself_total H | [8 empty] | self electric energy total H | [15 empty] | 0.1kWh |  |  |  |  | self electric energy total H
1144 |  |  | Eself_ total L | [8 empty] | self electric energy total L | [15 empty] | 0.1kWh |  |  |  |  | self electric energy total L
1145 |  |  | PSystem H | [8 empty] | System power H | [15 empty] | 0.1w |  |  |  |  | System power H
1146 |  |  | PSystem L | [8 empty] | System power L | [15 empty] | 0.1w |  |  |  |  | System power L
1147 |  |  | PSelf H | [8 empty] | self power H | [15 empty] | 0.1w |  |  |  |  | self power H
1148 |  |  | PSelf L | [8 empty] | self power L | [15 empty] | 0.1w |  |  |  |  | self power L
1149 |  |  | EPVAll_Today H | [8 empty] | PV electric energy today H
1150 |  |  | EPVAll_Today L | [8 empty] | PV electric energy today L
1151 |  |  | AcDischarge PackSn | [8 empty] | Discharge number |  |  | power |  |  | pack |  | serial |  | R | [5 empty] | /
1152 |  |  |  | Accdischarge power_H | [7 empty] | Cumulative discharge power high 16-bit byte | [9 empty] | R | [6 empty] | 0.1 | kWH
1153 |  |  |  | Accdischarge power_L | [7 empty] | Cumulative discharge power low 16-bit byte | [9 empty] | R | [6 empty] | 0.1 | kWH
1154 |  |  | AccCharge PackSn | [8 empty] | charge power pack serial number | [9 empty] | R | [5 empty] | /
1155 |  |  |  | AccCharge power_H | [7 empty] | Cumulative charge power high 16-bit byte | [9 empty] | R | [6 empty] | 0.1 | kWH
1156 |  |  |  | AccCharge power_L | [7 empty] | Cumulative charge power low 16-bit byte | [9 empty] | R | [6 empty] | 0.1 | kWH
1157 |  |  |  | FirstBattFaultSn | [8 empty] | FirstBattFaultSn | [8 empty] | R | [5 empty] | /
1158 |  |  |  | Second BattFaultSn | [8 empty] | Second BattFaultSn | [8 empty] | R | [5 empty] | /
1159 |  |  |  | Third BattFaultSn | [8 empty] | Third BattFaultSn | [8 empty] | R | [5 empty] | /
1160 |  |  |  | Fourth BattFaultSn | [8 empty] | Fourth BattFaultSn | [8 empty] | R | [5 empty] | /
1161 |  |  |  | Battery history fault code 1 | [8 empty] | Battery history fault code 1 | [8 empty] | R | [5 empty] | /
1162 |  |  |  | Battery history fault code 2 | [8 empty] | Battery history fault code 2 | [8 empty] | R | [5 empty] | /
1163 |  |  |  | Battery history fault code 3 | [8 empty] | Battery history fault code 3 | [8 empty] | R | [5 empty] | /
1164 |  |  |  | Battery history fault code 4 | [8 empty] | Battery history fault code 4 | [8 empty] | R | [5 empty] | /
1165 |  |  |  | Battery history fault code 5 | [8 empty] | Battery history fault code 5 | [8 empty] | R | [5 empty] | /
1166 |  |  |  | Battery history fault code 6 | [8 empty] | Battery history fault code 6 | [8 empty] | R | [5 empty] | /
1167 |  |  |  | Battery history fault code 7 | [8 empty] | Battery history fault code 7 | [8 empty] | R | [5 empty] | /
1168 |  |  |  | Battery history fault code 8 | [8 empty] | Battery history fault code 8 | [8 empty] | R | [5 empty] | /
1169 |  |  |  | Number of battery codes | [7 empty] | Number of battery codes PACK number + BIC forward and reverse codes | [9 empty] | R | [5 empty] | /
1170
…… |  |  | / | [8 empty] | / | [9 empty] | / | [5 empty] | / |  |  |  |  | reversed
1199 |  |  | NewEPowerCalc Flag | [8 empty] | Intelligent reading is used to identify software compatibility features | [20 empty] | 0 ： Old energy calculation； 1 ： new energy calculation
1200 |  |  | MaxCellVolt | [8 empty] | Maximum cell voltage | [9 empty] | R | [5 empty] | 0.001V
1201 |  |  | MinCellVolt | [8 empty] | Minimum cell voltage | [9 empty] | R | [5 empty] | 0.001V
1202 |  |  | ModuleNum | [8 empty] | Number of Battery modules | [9 empty] | R | [5 empty] | /
1203 |  |  | TotalCellNum | [8 empty] | Total number of cells | [9 empty] | R | [5 empty] | /
1204 |  |  | MaxVoltCellNo | [8 empty] | MaxVoltCellNo | [9 empty] | R | [5 empty] | /
1205 |  |  | MinVoltCellNo | [8 empty] | MinVoltCellNo | [9 empty] | R | [5 empty] | /
1206 |  |  | MaxTemprCell_ 10T | [8 empty] | MaxTemprCell_10T | [9 empty] | R | [5 empty] | 0.1℃
1207 |  |  | MinTemprCell_1 0T | [8 empty] | MinTemprCell_10T | [9 empty] | R | [5 empty] | 0.1℃
1208 |  |  | MaxTemprCellN o | [8 empty] | MaxTemprCellNo | [9 empty] | R | [5 empty] | /
1209 |  |  | MinTemprCellN o | [8 empty] | MinTemprCellNo | [9 empty] | R | [5 empty] | /
1210 |  |  | ProtectPackID | [8 empty] | Fault Pack ID | [9 empty] | R | [5 empty] | /
1211 |  |  | MaxSOC | [8 empty] | Parallel maximum SOC | [9 empty] | R | [5 empty] | 1%
1212 |  |  | MinSOC | [8 empty] | Parallel minimum SOC | [9 empty] | R | [5 empty] | 1%
1213 |  |  | BatProtect1Add | [8 empty] | BatProtect1Add | [9 empty] | R | [5 empty] | /
1214 |  |  | BatProtect2Add | [8 empty] | BatProtect2Add | [9 empty] | R | [5 empty] | /
1215 |  |  | BatWarn1Add | [8 empty] | BatWarn1Add | [9 empty] | R | [5 empty] | /
1216 |  |  | BMS_HighestSof tVersion | [8 empty] | BMS_HighestSoftVersion | [9 empty] | R | [5 empty] | /
1217 |  |  | BMS_Hardware Version | [8 empty] | BMS_HardwareVersion | [9 empty] | R | [5 empty] | /
1218 |  |  | BMS_RequestTy pe | [8 empty] | BMS_RequestType | [9 empty] | R | [5 empty] | /
…… |  |  | / | [8 empty] | / | [9 empty] | / | [5 empty] | / |  |  |  |  | reversed
1248 |  |  | bKeyAgingTestO kFlag | [8 empty] | Success sign of key detection before aging | [20 empty] | 1：Finished test 0 ： test not completed
1249 |  |  | / | [8 empty] | / | [9 empty] | / | [5 empty] | / |  |  |  |  | reversed
thirteen group for Storage power’s SPA
2000 |  |  | Inverter Status | [8 empty] | Inverter run state | [10 empty] | 0:waiting, 1:normal, 3:fault | [11 empty] | SPA
…… |  |  | reversed
2035 |  |  | Pac H | [8 empty] | Output power (high) | [17 empty] | 0.1W |  |  |  |  | SPA
2036 |  |  | Pac L | [8 empty] | Output power (low) | [17 empty] | 0.1W |  |  |  |  | SPA
2037 |  |  | Fac | [8 empty] | Grid frequency | [17 empty] | 0.01Hz |  |  |  |  | SPA
2038 |  |  | Vac1 | [8 empty] | Three/single phase grid voltage | [17 empty] | 0.1V |  |  |  |  | SPA
2039 |  |  | Iac1 | [8 empty] | Three/single phase grid output current | [17 empty] | 0.1A |  |  |  |  | SPA
2040 |  |  | Pac1 H | [8 empty] | Three/single phase grid output watt VA (high) | [17 empty] | 0.1VA |  |  |  |  | SPA
2041 |  |  | Pac1 L | [8 empty] | Three/single phase grid output watt VA(low) | [17 empty] | 0.1VA |  |  |  |  | SPA
…… |  |  | reversed
2053 |  |  | Eac today H | [8 empty] | Today generate energy (high) | [17 empty] | 0.1kWH |  |  |  |  | SPA
2054 |  |  | Eac today L | [8 empty] | Today generate energy (low) | [17 empty] | 0.1kWH |  |  |  |  | SPA
2055 |  |  | Eac total H | [8 empty] | Total generate energy (high) | [17 empty] | 0.1kWH |  |  |  |  | SPA
2056 |  |  | Eac total L | [8 empty] | Total generate energy (low) | [17 empty] | 0.1kWH |  |  |  |  | SPA
2057 |  |  | Time total H | [8 empty] | Work time total (high) | [17 empty] | 0.5s |  |  |  |  | SPA
2058 |  |  | Time total L | [8 empty] | Work time total (low) | [17 empty] | 0.5s |  |  |  |  | SPA
…… |  |  | reversed
2093 |  |  | Temp1 | [8 empty] | Inverter temperature | [17 empty] | 0.1C |  |  |  |  | SPA
2094 |  |  | Temp2 | [8 empty] | The inside IPM in inverter Temperature | [17 empty] | 0.1C |  |  |  |  | SPA
2095 |  |  | Temp3 | [8 empty] | Boost temperature | [17 empty] | 0.1C |  |  |  |  | SPA
2096 |  |  | Temp4 | [31 empty] | reserved
2097 |  |  | uwBatVolt_DSP | [8 empty] | BatVolt_DSP | [17 empty] | 0.1V |  |  |  |  | BatVolt(DSP)
2098 |  |  | P Bus Voltage | [8 empty] | P Bus inside Voltage | [17 empty] | 0.1V |  |  |  |  | SPA
2099 |  |  | N Bus Voltage | [8 empty] | N Bus inside Voltage | [17 empty] | 0.1V |  |  |  |  | SPA
2100 |  |  | RemoteCtrlEn | [8 empty] | / | [10 empty] | 0.Load First 1.BatFirst 2.Grid | [6 empty] | / |  |  |  |  | Remote setup enable
2101 |  |  | RemoteCtrlPow er | [8 empty] | / | [17 empty] | / |  |  |  |  | Remotely set power
2102 |  |  | Extra AC Power to grid_H | [8 empty] | Extra inverte AC Power to grid High | [10 empty] | For SPA connect inverter | [11 empty] | SPA used
2103 |  |  | Extra AC Power to grid_L | [8 empty] | Extrainverte AC Power to grid Low | [22 empty] | SPA used
2104 |  |  | Eextra_today H | [8 empty] | Extra inverter PowerTOUser_Extra today (high) | [10 empty] | R | [6 empty] | 0.1kWh |  |  |  |  | SPA |  | used
2105 |  |  | Eextra_today L | [8 empty] | Extra inverter PowerTOUser_Extra today (low) | [10 empty] | R | [6 empty] | 0.1kWh |  |  |  |  | SPA |  | used
2106 |  |  | Eextra_total H | [8 empty] | Extra inverter PowerTOUser_Extratotal(high) | [17 empty] | 0.1kWh |  |  |  |  | SPA |  | used
2107 |  |  | Eextra_total L | [8 empty] | Extra inverter PowerTOUser_Extra total(low) | [17 empty] | 0.1kWh |  |  |  |  | SPA |  | used
2108 |  |  | Esystem_today H | [8 empty] | System electric energy today H | [17 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today H
2109 |  |  | Esystem_ L |  |  |  |  | today |  |  |  | System electric energy today L | [17 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy today L
2110 |  |  | Esystem_total H | [8 empty] | System electric energy total H | [17 empty] | 0.1kWh |  |  |  |  | SPA used System
electric energy total H
2111 |  |  | Esystem_ total L | [8 empty] | System electric energy total L | [17 empty] | 0.1kWh |  |  |  |  | SPA used System electric energy total L
2112 |  |  | EACharge_Today _H | [8 empty] | ACCharge energy today | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2113 |  |  | EACharge_Today _L | [8 empty] | ACCharge energy today | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2114 |  |  | EACharge_Total _H | [8 empty] | ACCharge energy total | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2115 |  |  | EACharge_Total _L | [8 empty] | ACCharge energy total | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2116 |  |  | AC charge Power_H | [8 empty] | Grid power to local load | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2117 |  |  | AC charge Power_L | [8 empty] | Grid power to local load | [17 empty] | 0.1kwh |  |  |  |  | Storage Power
2118 |  |  | Priority | [8 empty] | 0:Load First 1:Battery First 2:Grid First | [22 empty] | Storage Power
2119 |  |  | Battery Type | [8 empty] | 0：Lead-acid 1：Lithium battery | [22 empty] | Storage Power
2120 |  |  | AutoProofreadC MD | [8 empty] | Aging mode | [22 empty] | Storage Power
… |  |  | reserved | [31 empty] | reserved
2124 |  |  | reserved | [31 empty] | reserved
Use for TL-X and TL-XH
3000 |  |  | Inverter Status | [8 empty] | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: Self-test mode, optional 2: Reserved 3：SysFault module 4: Flash module 5：PVBATOnline module: 6：BatOnline module
7：PVOfflineMode 8：BatOfflineMode The lower 8 bits indicate the machine status (web page display) 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus;
3001 |  |  | Ppv H | [8 empty] | PV total power | [17 empty] | 0.1W
3002 |  |  | Ppv L
3003 |  |  | Vpv1 | [8 empty] | PV1 voltage | [17 empty] | 0.1V
3004 |  |  | Ipv1 | [8 empty] | PV1 input current | [17 empty] | 0.1A
3005 |  |  | Ppv1 H | [8 empty] | PV1 power | [17 empty] | 0.1W
3006 |  |  | Ppv1 L
3007 |  |  | Vpv2 | [8 empty] | PV2 voltage | [17 empty] | 0.1V
3008 |  |  | Ipv2 | [8 empty] | PV2 input current | [17 empty] | 0.1A
3009 |  |  | Ppv2 H | [8 empty] | PV2 power | [17 empty] | 0.1W
3010 |  |  | Ppv2 L
3011 |  |  | Vpv3 | [8 empty] | PV3 voltage | [17 empty] | 0.1V
3012 |  |  | Ipv3 | [8 empty] | PV3 input current | [17 empty] | 0.1A
3013 |  |  | Ppv3 H | [8 empty] | PV3 power | [17 empty] | 0.1W
3014 |  |  | Ppv3 L
3015 |  |  | Vpv4 | [8 empty] | PV4 voltage
3016 |  |  | Ipv4 | [8 empty] | PV4 input current
3017 |  |  | Ppv4H | [8 empty] | PV4 power
3018 |  |  | Ppv4L
3019 |  |  | Psys H | [8 empty] | System output power | [17 empty] | 0.1W
3020 |  |  | Psys L
3021 |  |  | Qac H | [8 empty] | reactive power | [17 empty] | 0.1Var
3022 |  |  | Qac L
3023 |  |  | Pac H | [8 empty] | Output power | [17 empty] | 0.1W |  |  |  | Output power
3024 |  |  | Pac L
3025 |  |  | Fac | [8 empty] | Grid frequency | [17 empty] | 0.01Hz |  |  |  | Grid frequency
3026 |  |  | Vac1 | [8 empty] | Three/single phase grid voltage | [17 empty] | 0.1V |  |  |  | Three/single phase grid voltage
3027 |  |  | Iac1 | [8 empty] | Three/single phase grid output current | [17 empty] | 0.1A |  |  |  | Three/single
phase grid output current
3028 |  |  | Pac1 H | [8 empty] | Three/single phase grid output watt VA | [17 empty] | 0.1VA |  |  |  | Three/single phase grid output watt VA
3029 |  |  | Pac1 L
3030 |  |  | Vac2 | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V |  |  |  | Three phase grid voltage
3031 |  |  | Iac2 | [8 empty] | Three phase grid output current | [17 empty] | 0.1A |  |  |  | Three phase grid output current
3032 |  |  | Pac2 H | [8 empty] | Three phase grid output power | [17 empty] | 0.1VA |  |  |  | Three phase grid output power
3033 |  |  | Pac2 L
3034 |  |  | Vac3 | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V |  |  |  | Three phase grid voltage
3035 |  |  | Iac3 | [8 empty] | Three phase grid output current | [17 empty] | 0.1A |  |  |  | Three phase grid output current
3036 |  |  | Pac3 H | [8 empty] | Three phase grid output power | [17 empty] | 0.1VA |  |  |  | Three phase grid output power
3037 |  |  | Pac3 L
3038 |  |  | Vac_RS | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V
3039 |  |  | Vac_ST | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V
3040 |  |  | Vac_TR | [8 empty] | Three phase grid voltage | [17 empty] | 0.1V
3041 |  |  | Ptouser total H | [8 empty] | Total forward power | [17 empty] | 0.1W |  |  |  | Total forward power
3042 |  |  | Ptouser total L
3043 |  |  | Ptogrid total H | [8 empty] | Total reverse power | [17 empty] | 0.1W |  |  |  | Total reverse power
3044 |  |  | Ptogrid total L
3045 |  |  | Ptoload total H | [8 empty] | Total load power | [17 empty] | 0.1W |  |  |  | Total load power
3046 |  |  | Ptoload total L
3047 |  |  | Time total H | [8 empty] | Work time total | [17 empty] | 0.5s
3048 |  |  | Time total L
3049 |  |  | Eac today H | [8 empty] | Today generate energy | [17 empty] | 0.1kWh |  |  |  | Today generate energy
3050 |  |  | Eac today L
3051 |  |  | Eac total H | [8 empty] | Total generate energy | [17 empty] | 0.1kWh |  |  |  | Total generate
3052 |  |  | Eac total L
energy
3053 |  |  | Epv_total H | [8 empty] | PV energy total | [17 empty] | 0.1kWh |  |  |  | PV energy total
3054 |  |  | Epv_total L
3055 |  |  | Epv1_today H | [8 empty] | PV1 energy today | [17 empty] | 0.1kWh
3056 |  |  | Epv1_today L
3057 |  |  | Epv1_total H | [8 empty] | PV1 energy total | [17 empty] | 0.1kWh
3058 |  |  | Epv1_total L
3059 |  |  | Epv2_today H | [8 empty] | PV2 energy today | [17 empty] | 0.1kWh
3060 |  |  | Epv2_today L
3061 |  |  | Epv2_total H | [8 empty] | PV2 energy total | [17 empty] | 0.1kWh
3062 |  |  | Epv2_total L
3063 |  |  | Epv3_today H | [8 empty] | PV3 energy today | [17 empty] | 0.1kWh
3064 |  |  | Epv3_today L
3065 |  |  | Epv3_total H | [8 empty] | PV3 energy total | [17 empty] | 0.1kWh
3066 |  |  | Epv3_total L
3067 |  |  | Etouser_today H | [8 empty] | Today energy to user | [17 empty] | 0.1kWh |  |  |  | Today energy to user
3068 |  |  | Etouser_today L
3069 |  |  | Etouser_total H | [8 empty] | Total energy to user | [17 empty] | 0.1kWh |  |  |  | Total energy to user
3070 |  |  | Etouser_total L
3071 |  |  | Etogrid_today H | [8 empty] | Today energy to grid | [17 empty] | 0.1kWh |  |  |  | Today energy to grid
3072 |  |  | Etogrid_today L
3073 |  |  | Etogrid_total H | [8 empty] | Total energy to grid | [17 empty] | 0.1kWh |  |  |  | Total energy to grid
3074 |  |  | Etogrid_total L
3075 |  |  | Eload_today H | [8 empty] | Today energy of user load | [17 empty] | 0.1kWh |  |  |  | Today energy of user load
3076 |  |  | Eload_today L
3077 |  |  | Eload_total H | [8 empty] | Total energy of user load | [17 empty] | 0.1kWh |  |  |  | Total energy of user load
3078 |  |  | Eload_total L
3079 |  |  | Epv4_today H | [8 empty] | PV4 energy today | [17 empty] | 0.1kWh
3080 |  |  | Epv4_today L
3081 |  |  | Epv4_total H | [8 empty] | PV4 energy total | [17 empty] | 0.1kWh
3082 |  |  | Epv4_total L
3083 |  |  | Epv_today H | [8 empty] | PV energy today | [17 empty] | 0.1kWh
3084 |  |  | Epv_today L
3085 |  |  | Reserved
3086 |  |  | DeratingMode | [8 empty] | DeratingMode | [21 empty] | 0:cNOTDerate 1:cPVHighDer ate 2: cPowerCon stantDerate 3: cGridVHigh Derate 4:cFreqHighD erate 5:cDcSoureM odeDerate 6:cInvTemprD erate 7:cActivePow erOrder 8:cLoadSpeed Process 9:cOverBack byTime 10:cInternalT emprDerate 11:cOutTemp rDerate 12:cLineImpe CalcDerate 13: cParallelA ntiBackflowD erate 14:cLocalAnti BackflowDera te 15:cBdcLoadP riDerate 16:cChkCTErr Derate
3087 |  |  | ISO | [8 empty] | PV ISO value | [17 empty] | 1KΩ
3088 |  |  | DCI_R | [8 empty] | R DCI Curr | [17 empty] | 0.1mA
3089 |  |  | DCI_S | [8 empty] | S DCI Curr | [17 empty] | 0.1mA
3090 |  |  | DCI_T | [8 empty] | T DCI Curr | [17 empty] | 0.1mA
3091 |  |  | GFCI | [8 empty] | GFCI Curr | [17 empty] | 1mA
3092 |  |  | Bus Voltage | [8 empty] | total bus voltage | [17 empty] | 0.1V
3093 |  |  | Temp1 | [8 empty] | Inverter temperature | [17 empty] | 0.1℃
3094 |  |  | Temp2 | [8 empty] | The inside IPM in inverter temperature | [17 empty] | 0.1℃
3095 |  |  | Temp3 | [8 empty] | Boost temperature | [17 empty] | 0.1℃
3096 |  |  | Temp4 | [8 empty] | Reserved | [17 empty] | 0.1℃
3097 |  |  | Temp5 | [8 empty] | Commmunication broad temperature | [17 empty] | 0.1℃
3098 |  |  | P Bus Voltage | [8 empty] | P Bus inside Voltage | [17 empty] | 0.1V
3099 |  |  | N Bus Voltage | [8 empty] | N Bus inside Voltage | [17 empty] | 0.1V
3100 |  |  | IPF | [8 empty] | Inverter output PF now | [21 empty] | 0-20000
3101 |  |  | RealOPPercent | [8 empty] | Real Output power Percent | [17 empty] | 1% |  |  |  | 1~100
3102 |  |  | OPFullwatt H | [8 empty] | Output Maxpower Limited | [17 empty] | 0.1W |  |  |  | Output Maxpower Limited
3103 |  |  | OPFullwatt L
3104 |  |  | StandbyFlag | [8 empty] | Inverter standby flag | [17 empty] | bitfield |  |  |  | bit0:turn off Order； bit1:PV Low； bit2:AC Volt/Freq out of scope； bit3~bit7 ： Reserved
3105 |  |  | Fault Maincode | [8 empty] | Inverter fault maincode
3106 |  |  | Warn Maincode | [8 empty] | Inverter Warning maincode
3107 |  |  | Fault Subcode | [8 empty] | Inverter fault subcode | [17 empty] | bitfield
3108 |  |  | Warn Subcode | [8 empty] | Inverter Warning subcode | [17 empty] | bitfield
3109 | [29 empty] | bitfield
3110 | [29 empty] | bitfield
3111 |  |  | uwPresentFFTVa lue [CHANNEL_A ] | [8 empty] | PresentFFTValue [CHANNEL_A] | [17 empty] | bitfield
3112 |  |  | bAfciStatus | [8 empty] | AFCI Status | [21 empty] | 0 ： waiting state 1：self-check 2 ： Detection of arcing state 3：fault state 4 ： update state
3113 |  |  | uwStrength[CHA NNEL_A] | [8 empty] | AFCI Strength[CHANNEL_A]
3114 |  |  | uwSelfCheckVal ue[CHANNEL_A] | [8 empty] | AFCI SelfCheck[CHANNEL_A]
3115 |  |  | inv start delay time | [8 empty] | inv start delay time | [17 empty] | 1S |  |  |  | inv start delay time
3116 |  |  | Reserved
3117 |  |  | Reserved
3118 |  |  | BDC_OnOffState | [8 empty] | BDC connect state | [21 empty] | 0:No BDC Connect 1:BDC1 Connect 2:BDC2 Connect 3:BDC1+BDC2 Connect
3119 |  |  | DryContactState | [8 empty] | Current status of DryContact | [21 empty] | Current status of DryContact 0: turn off; 1: turn on;
3120 |  |  | Reserved
3121 |  |  | Pself H | [8 empty] | self-use power | [17 empty] | 0.1W
3122 |  |  | Pself L
3123 |  |  | Esys_today H | [8 empty] | System energy today | [17 empty] | 0.1kwh
3124 |  |  | Esys_today L
3125 |  |  | Edischr_today H | [8 empty] | Today discharge energy | [17 empty] | 0.1kWh |  |  |  | Today discharge energy
3126 |  |  | Edischr_today L
3127 |  |  | Edischr_total H | [8 empty] | Total discharge energy | [17 empty] | 0.1kWh |  |  |  | Total discharge energy
3128 |  |  | Edischr_total L
3129 |  |  | Echr_today H | [8 empty] | Charge energy today | [17 empty] | 0.1kWh |  |  |  | Charge energy today
3130 |  |  | Echr_today L
3131 |  |  | Echr_total H | [8 empty] | Charge energy total | [17 empty] | 0.1kWh |  |  |  | Charge energy total
3132 |  |  | Echr_total L
3133 |  |  | Eacchr_today H | [8 empty] | Today energy of AC charge | [17 empty] | 0.1kWh |  |  |  | Today energy of AC charge
3134 |  |  | Eacchr_today L
3135 |  |  | Eacchr_total H | [8 empty] | Total energy of AC charge | [17 empty] | 0.1kWh |  |  |  | Total energy of AC charge
3136 |  |  | Eacchr_total L
3137 |  |  | Esys_total H
3138 |  |  | Esys_total L | [8 empty] | Total energy of system output \ | [17 empty] | 0.1kWh
3139 |  |  | Eself_today H | [8 empty] | Today energy of Self output | [17 empty] | 0.1kWh
3140 |  |  | Eself_today L
3141 |  |  | Eself_total H | [8 empty] | Total energy of Self output | [17 empty] | 0.1kwh
3142 |  |  | Eself_ total L
3143 |  |  | Reserved
3144 |  |  | Priority | [8 empty] | Word Mode | [21 empty] | 0 LoadFirst 1 BatteryFirs t 2 GridFirst
3145 |  |  | EPS Fac | [8 empty] | UPS frequency | [17 empty] | 0.01Hz
3146 |  |  | EPS Vac1 | [8 empty] | UPS phase R output voltage | [17 empty] | 0.1V
3147 |  |  | EPS Iac1 | [8 empty] | UPS phase R output current | [17 empty] | 0.1A
3148 |  |  | EPS Pac1 H | [8 empty] | UPS phase R output power | [17 empty] | 0.1VA
3149 |  |  | EPS Pac1 L
3150 |  |  | EPS Vac2 | [8 empty] | UPS phase S output voltage | [17 empty] | 0.1V
3151 |  |  | EPS Iac2 | [8 empty] | UPS phase S output current | [17 empty] | 0.1A
3152 |  |  | EPS Pac2 H | [8 empty] | UPS phase S output power | [17 empty] | 0.1VA
3153 |  |  | EPS Pac2 L
3154 |  |  | EPS Vac3 | [8 empty] | UPS phase T output voltage | [17 empty] | 0.1V
3155 |  |  | EPS Iac3 | [8 empty] | UPS phase T output current | [17 empty] | 0.1A
3156 |  |  | EPS Pac3 H | [8 empty] | UPS phase T output power | [17 empty] | 0.1VA
3157 |  |  | EPS Pac3 L
3158 |  |  | EPS Pac H | [8 empty] | UPS output power | [17 empty] | 0.1VA
3159 |  |  | EPS Pac L
3160 |  |  | Loadpercent | [8 empty] | Load percent of UPS ouput | [17 empty] | 0.1%
3161 |  |  | PF | [8 empty] | Power factor | [17 empty] | 0.1
3162 |  |  | DCV | [8 empty] | DC voltage | [17 empty] | 1mV
3163 |  |  | Reserved
3164 |  |  | NewBdcFlag | [8 empty] | Whether to parse BDC data separately | [21 empty] | 0: Don't need 1：need
3165 |  |  | BDCDeratingMo de | [8 empty] | BDCDeratingMode： 0: Normal, unrestricted 1：Standby or fault 2：Maximum battery current limit (discharge) 3：Battery discharge Enable (Discharge) 4：High bus discharge derating
(discharge) 5：High temperature discharge derating (discharge) 6：System warning No discharge (discharge) 7-15 Reserved (Discharge) 16：Maximum charging current of battery (charging) 17：High Temperature (LLC and Buckboost) (Charging) 18：Final soft charge 19：SOC setting limits (charging) 20：Battery low temperature (charging) 21：High bus voltage (charging) 22：Battery SOC (charging) 23: Need to charge (charge） 24: System warning not charging (charging) 25-29：Reserve (charge)
3166 |  |  | SysState_Mode | [8 empty] | System work State and mode The upper 8 bits indicate the mode; 0：No charge and discharge； 1：charge； 2：Discharge； The lower 8 bits represent the status; 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3：FlashStatus; | [21 empty] | BDC1
3167 |  |  | FaultCode | [8 empty] | Storge device fault code
3168 |  |  | WarnCode | [8 empty] | Storge device warning code
3169 |  |  | Vbat | [8 empty] | Battery voltage | [17 empty] | 0.01V
3170 |  |  | Ibat | [8 empty] | Battery current | [17 empty] | 0.1A
3171 |  |  | SOC | [8 empty] | State of charge Capacity | [17 empty] | 1%
3172 |  |  | Vbus1 | [8 empty] | Total BUS voltage | [17 empty] | 0.1V
3173 |  |  | Vbus2 | [8 empty] | On the BUS voltage | [17 empty] | 0.1V
3174 |  |  | Ibb | [8 empty] | BUCK-BOOST Current | [17 empty] | 0.1A
3175 |  |  | Illc | [8 empty] | LLC Current | [17 empty] | 0.1A
3176 |  |  | TempA | [8 empty] | Temperture A | [17 empty] | 0.1℃
3177 |  |  | TempB | [8 empty] | Temperture B | [17 empty] | 0.1℃
3178 |  |  | Pdischr H | [8 empty] | Discharge power | [17 empty] | 0.1W
3179 |  |  | Pdischr L
3180 |  |  | Pchr H | [8 empty] | Charge power | [17 empty] | 0.1W
3181 |  |  | Pchr L
3182 |  |  | Edischr_total H | [8 empty] | Discharge total energy of storge device | [17 empty] | 0.1kWh
3183 |  |  | Edischr_total L
3184 |  |  | Echr_total H | [8 empty] | Charge total energy of storge device | [17 empty] | 0.1kWh
3185 |  |  | Echr_total L
3186 |  |  | Reserved | [8 empty] | Reserved
3187 |  |  | BDC1_Flag | [8 empty] | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code
3188 |  |  | Vbus2 | [8 empty] | Lower BUS voltage | [17 empty] | 0.1V
3189 |  |  | BmsMaxVoltCell No | [8 empty] | BmsMaxVoltCellNo
3190 |  |  | BmsMinVoltCell No | [8 empty] | BmsMinVoltCellNo
3191 |  |  | BmsBatteryAvgT emp | [8 empty] | BmsBatteryAvgTemp
3192 |  |  | BmsMaxCellTem p | [8 empty] | BmsMaxCellTemp | [17 empty] | 0.1°C
3193 |  |  | BmsBatteryAvgT emp | [8 empty] | BmsBatteryAvgTemp | [17 empty] | 0.1°C
3194 |  |  | BmsMaxCellTem p | [8 empty] | BmsMaxCellTemp
3195 |  |  | BmsBatteryAvgT emp | [8 empty] | BmsBatteryAvgTemp
3196 |  |  | BmsMaxSOC | [8 empty] | BmsMaxSOC | [17 empty] | 1%
3197 |  |  | BmsMinSOC | [8 empty] | BmsMinSOC | [17 empty] | 1%
3198 |  |  | ParallelBatteryN um | [8 empty] | ParallelBatteryNum
3199 |  |  | BmsDerateReas on | [8 empty] | BmsDerateReason
3200 |  |  | BmsGaugeFCC （Ah） | [8 empty] | BmsGaugeFCC（Ah）
3201 |  |  | BmsGaugeRM （Ah） | [8 empty] | BmsGaugeRM（Ah）
3202 |  |  | BmsError | [8 empty] | BMS Protect1
3203 |  |  | BmsWarn | [8 empty] | BMSWarn1
3204 |  |  | BmsFault | [8 empty] | BMS Fault1
3205 |  |  | BmsFault2 | [8 empty] | BMS Fault2
3206 |  |  | Reserved
3207 |  |  | Reserved
3208 |  |  | Reserved
3209 |  |  | Reserved
3210 |  |  | BatIsoStatus | [8 empty] | Battery ISO detection status | [21 empty] | 0：Not detected 1 ： Detection completed
3211 |  |  | BattNeedCharge RequestFlag | [8 empty] | battery work request | [17 empty] | bit0:1： Prohibit chargin g，0： Allow the chargin g bit1:1： Enable strong charge， 0： disable strong charge bit2:1： Enable strong charge2 0： disable strong charge
2 bit8:1: Dischar ge is prohibit ed， 0： allow discharg e bit9:1： Turn on power reductio n 0： turn off power reductio n；
3212 |  |  | BMS_Status | [8 empty] | battery working status | [10 empty] | R | [10 empty] | 0: dormancy 1:Charge 2:Discharge 3:free 4:standby 5:Soft start 6:fault 7:update
3213 |  |  | BmsError2 | [8 empty] | BMS Protect2 | [10 empty] | R | [6 empty] | 1
3214 |  |  | BmsWarn2 | [8 empty] | BMS Warn2 | [10 empty] | R | [6 empty] | 1
3215 |  |  | BMS_SOC | [8 empty] | BMS SOC | [10 empty] | R | [6 empty] | 1%
3216 |  |  | BMS_BatteryVol t | [8 empty] | BMS BatteryVolt | [10 empty] | R | [6 empty] | 0.01V
3217 |  |  | BMS_BatteryCur r | [8 empty] | BMS BatteryCurr | [10 empty] | R | [6 empty] | 0.01A
3218 |  |  | BMS_BatteryTe mp | [8 empty] | battery cell maximum temperature | [10 empty] | R | [6 empty] | 0.1℃
3219 |  |  | BMS_MaxCurr | [8 empty] | Maximum charging current | [10 empty] | R | [6 empty] | 0.01A
3220 |  |  | BMS_MaxDischr Curr | [8 empty] | Maximum discharge current | [10 empty] | R | [6 empty] | 0.01A
3221 |  |  | BMS_CycleCnt | [8 empty] | BMSCycleCnt | [10 empty] | R | [6 empty] | 1
3222 |  |  | BMS_SOH | [8 empty] | BMS SOH | [10 empty] | R | [6 empty] | 1
3223 |  |  | BMS_ChargeVol tLimit | [8 empty] | Battery charging voltage limit value | [10 empty] | R | [6 empty] | 0.01V
3224 |  |  | BMS_Discharge VoltLimit | [8 empty] | Battery discharge voltage limit value
3225 |  |  | Bms Warn3 | [8 empty] | BMS Warn 3 | [10 empty] | R | [6 empty] | 1
3226 |  |  | Bms Error3 | [8 empty] | BMS Protect3 | [10 empty] | R | [6 empty] | 1
3227 |  |  | Reserved
3228 |  |  | Reserved
3229 |  |  | Reserved
3230 |  |  | BMSSingleVoltM ax | [8 empty] | BMS Battery SingleVoltMax | [10 empty] | R | [6 empty] | 0.001V
3231 |  |  | BMSSingleVoltM in | [8 empty] | BMS Battery SingleVoltMin | [10 empty] | R | [6 empty] | 0.001V
3232 |  |  | BatLoadVolt | [8 empty] | Battery LoadVolt | [10 empty] | R | [6 empty] | 0.01V |  |  |  | [0，650.00]
3233
3234 |  |  | Debug data1 | [8 empty] | Debug data1 | [10 empty] | R
3235 |  |  | Debug data2 | [8 empty] | Debug data2 | [10 empty] | R
3236 |  |  | Debug data3 | [8 empty] | Debug data3 | [10 empty] | R
3237 |  |  | Debug data4 | [8 empty] | Debug data4 | [10 empty] | R
3238 |  |  | Debug data5 | [8 empty] | Debug data5 | [10 empty] | R
3239 |  |  | Debug data6 | [8 empty] | Debug data6 | [10 empty] | R
3240 |  |  | Debug data7 | [8 empty] | Debug data7 | [10 empty] | R
3241 |  |  | Debug data8 | [8 empty] | Debug data8 | [10 empty] | R
3242 |  |  | Debug data9 | [8 empty] | Debug data9 | [10 empty] | R
3243 |  |  | Debug data10 | [8 empty] | Debug data10 | [10 empty] | R
3244 |  |  | Debug data10 | [8 empty] | Debug data10 | [10 empty] | R
3245 |  |  | Debug data12 | [8 empty] | Debug data12 | [10 empty] | R
3246 |  |  | Debug data13 | [8 empty] | Debug data13 | [10 empty] | R
3247 |  |  | Debug data14 | [8 empty] | Debug data14 | [10 empty] | R
3248 |  |  | Debug data15 | [8 empty] | Debug data15 | [10 empty] | R
3249 |  |  | Debug data16 | [8 empty] | Debug data16 | [10 empty] | R
3250 |  |  | Pex1H | [8 empty] | PV inverter 1 output power H | [10 empty] | R | [6 empty] | 0.1W
3251 |  |  | Pex1L | [8 empty] | PV inverter 1 output power L | [10 empty] | R | [6 empty] | 0.1W
3252 |  |  | Pex2H | [8 empty] | PV inverter 2 output power H | [10 empty] | R | [6 empty] | 0.1W
3253 |  |  | Pex2L | [8 empty] | PV inverter 2 output power L | [10 empty] | R | [6 empty] | 0.1W
3254 |  |  | Eex1TodayH | [8 empty] | PV inverter 1 energy Today H | [10 empty] | R | [6 empty] | 0.1kWh
3255 |  |  | Eex1TodayL | [8 empty] | PV inverter 1 energy Today L | [10 empty] | R | [6 empty] | 0.1kWh
3256 |  |  | Eex2TodayH | [8 empty] | PV inverter 2 energy Today H | [10 empty] | R | [6 empty] | 0.1kWh
3257 |  |  | Eex2TodayL | [8 empty] | PV inverter 2 energy Today L | [10 empty] | R | [6 empty] | 0.1kWh
3258 |  |  | Eex1TotalH | [8 empty] | PV inverter 1 energy Total H | [10 empty] | R | [6 empty] | 0.1kWh
3259 |  |  | Eex1TotalL | [8 empty] | PV inverter 1 energy Total L | [10 empty] | R | [6 empty] | 0.1kWh
3260 |  |  | Eex2TotalH | [8 empty] | PV inverter 2 energy Total H | [10 empty] | R | [6 empty] | 0.1kWh
3261 |  |  | Eex2TotalL | [8 empty] | PV inverter 2 energy Total L | [10 empty] | R | [6 empty] | 0.1kWh
3262 |  |  | uwBatNo | [8 empty] | battery pack number | [10 empty] | R | [10 empty] | BDC reports are updated every 15 minutes
3263 |  |  | BatSerialNum1 | [8 empty] | Battery pack serial numberSN[0]SN[1] | [10 empty] | R | [10 empty] | BDC reports are updated every 15 minutes
3264 |  |  | BatSerialNum2 | [8 empty] | Battery pack serial numberSN[2]SN[3] | [10 empty] | R
3265 |  |  | BatSerialNum3 | [8 empty] | Battery pack serial numberSN[4]SN[5] | [10 empty] | R
3266 |  |  | BatSerialNum4 | [8 empty] | Battery pack serial numberSN[6]SN[7] | [10 empty] | R
3267 |  |  | BatSerialNum5 | [8 empty] | Battery pack serial numberSN[8]SN[9] | [10 empty] | R
3268 |  |  | BatSerialNum6 | [8 empty] | Battery pack serial numberSN[10]SN[11] | [10 empty] | R
3269 |  |  | BatSerialNum7 | [8 empty] | Battery pack serial numberSN[12]SN[13] | [10 empty] | R
3270 |  |  | BatSerialNum8 | [8 empty] | Battery pack serial numberSN[14]SN[15] | [10 empty] | R
3271- 3279 |  |  | Reserve | [8 empty] | Reserve
3280 |  |  | bClrTodayDataFl ag | [8 empty] | Clear day data flag | [10 empty] | R | [10 empty] | Data of the current day that the server
determines whether to clear. 0:not cleared. 1: Clear.
BDC and BMS information (support up to 10 PARALLEL BDCS)
4000- 4107 |  |  | 1 | [8 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4108- 4215 |  |  | 2 | [8 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
…… | [11 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4864- 4971 |  |  | 9 | [8 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4972- 5079 |  |  | 10 | [8 empty] | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
5 Set address
Refer to the Inverter user manual. Always is : Knock the pv inverter to let the lcd display to the “COM Addr: xxx”, then double knock, if displays “Move”, you should another double knock, until it displays a address number, then you can give a single knock to change the address, this address will be remembered when the lcd backlight off.
6 Notice
1) It can drive mostly 32 pv inverters for one rs485 comport. 2) There are only read input and hold registers commands even the newest version.
3) App user could only care the input register. 4) App user could not care the holding registers. 5) Except the CEI0-21 and VDE-AR-N 4105 power management registers, you should refer the manufactory’s suggestion when writing the other registers;

## holding registers
4 Register map It is 16bits (two bytes) unsigned integer for each holding and input register; 4.1 Holding Reg
Registe r NO. | Variable Name | Description |  | Value |  | Unit |  | Initial value | Note
First group
0 | OnOff | Remote On/Off . On（1）；Of（f 0）Inverter On（3）；Off（2）BDC |  | 0、1、2、 3 |  |  |  | 1 | The inverter can be switched on and off, and the BDC can be switched on and off for the batt ready function.
1 | SaftyFuncEn | Bit0: SPI enable Bit1: AutoTestStart Bit2: LVFRT enable Bit3:FreqDerating Enable Bit4: Softstart enable Bit5: DRMS enable Bit6:PowerVoltFunc Enable Bit7: HVFRT enable Bit8:ROCOF enable Bit9: Recover FreqDeratingMode Enable |  | 0 : disable 1: enable |  |  |  |  | SPI: system protection interface Bit0~3:for CEI0-21 Bit4~6:for SAA
Bit10：Split phase enable
Bit10~15:预留
2 | PF CMD memory state | Set Holding register3,4,5,99 CMD will be memory or not(1/0), if not, these settings are the initial value. |  | 0or1 |  |  |  | 0 | Means these settings will be acting or not when next power on
3 | Active P Rate | Inverter Max output active power percent |  | 0-100 or 255 |  | % |  | 255 | 255: power is not be limited
4 | Reactive P Rate | Inverter max output reactive power percent |  | -100-100 or 255 |  | % |  | 255 | 255: power is not be limited
5 | Power factor | Inverter output power factor’s 10000 times |  | 0-20000, 0-10000 is underexci ted, other is overexcit ed |  |  |  | 0
6 | Pmax H | Normal power (high) |  |  |  | 0.1VA
7 | Pmax L | Normal power (low) |  |  |  | 0.1VA
8 | Vnormal | Normal work PV voltage |  |  |  | 0.1V
9 | Fw version H | Firmware version (high) |  |  |  | ASCII
10 | Fw version M | Firmware version (middle)
11 | Fw version L | Firmware version (low)
12 | Fw version2 H | Control Firmware version (high) |  |  |  | ASCII
13 | Fw version2 M | Control Firmware version (middle)
14 | Fw version2 L | Control Firmware version (low)
15 | LCD language | LCD language |  | 0-5 |  |  |  |  | 0: Italian; 1: English; 2: German; 3: Spanish; 4: French; 5: Chinese; 6：Polish 7：Portugues 8：Hungary
16 | CountrySele cted | Country Selected or not |  | 0: need to select; 1: have selected
17 | Vpv start | Input start voltage |  |  |  | 0.1V
18 | Time start | Start time |  |  |  | 1s
19 | RestartDelay Time | Restart Delay Time after fault back; |  |  |  | 1s
20 | wPowerStart Slope | Power start slope |  | 1-1000 |  | 0.1%
21 | wPowerRest artSlopeEE | Power restart slope |  | 1-1000 |  | 0.1%
22 | wSelectBaud rate | Select communicationbaudrat e 0: 9600bps 1:38400bps |  | 0-1 |  |  |  | 0
23 | Serial NO | Serial number 1-2 |  |  |  | ASCII
24 | Serial NO | Serial number 3-4
25 | Serial NO | Serial number 5-6
26 | Serial NO | Serial number 7-8
27 | Serial NO | Serial number 9-10
28 | Module H | Inverter Module (high) |  | &*5
29 | Module L | Inverter Module (low) |  | &*5
30 | Com Address | Communicate address |  | 1-254 |  |  |  | 1
31 | FlashStart | Update firmware |  | 1
32 | Reset User Info | Reset User Information |  | 0x0001
33 | Reset to factory | Reset to factory |  | 0x0001
34 | Manufacture r Info 8 | Manufacturer information (high) |  |  |  | ASCII
35 | Manufacture r Info 7 | Manufacturer information (middle)
36 | Manufacture r Info 6 | Manufacturer information (low)
37 | Manufacture r Info 5 | Manufacturer information (high)
38 | Manufacture r Info 4 | Manufacturer information (middle)
39 | Manufacture r Info3 | Manufacturer information (low)
40 | Manufacture r Info 2 | Manufacturer information (low)
41 | Manufacture r Info 1 | Manufacturer information (high)
42 | bfailsafeEn; | G100 fail safe |  | Enable:1 Disable:0 |  |  |  |  | English G100 fail safe set
43 | DTC | Device Type Code |  | &*6
44 | TP | Input tracker num and output phase num |  | Eg:0x020 3 is two MPPT and 3ph output
45 | Sys Year | System time-year |  | Year offset is 0 |  |  |  |  | Local time
46 | Sys Month | System time- Month
47 | Sys Day | System time- Day
48 | Sys Hour | System time- Hour
49 | Sys Min | System time- Min
50 | Sys Sec | System time- Second
51 | Sys Weekly | System Weekly |  | 0-6
52 | Vac low | Grid voltage low limit protect |  |  |  | 0.1V
53 | Vac high | Grid voltage high limit protect |  |  |  | 0.1V
54 | Fac low | Grid frequency low limit protect |  |  |  | 0.01 Hz
55 | Fac high | Grid high frequencylimit protect |  |  |  | 0.01 Hz
56 | Vac low 2 | Grid voltage low limit protect 2 |  |  |  | 0.1V
57 | Vac high 2 | Grid voltage high limit protect 2 |  |  |  | 0.1V
58 | Fac low 2 | Grid frequency low limit protect 2 |  |  |  | 0.01 Hz
59 | Fac high 2 | Grid high frequency limit protect 2 |  |  |  | 0.01 Hz
60 | Vac low 3 | Grid voltage low limit protect 3 |  |  |  | 0.1V
61 | Vac high 3 | Grid voltage high limit protect 3 |  |  |  | 0.1V
62 | Fac low 3 | Grid frequency low limit protect 3 |  |  |  | 0.01Hz
63 | Fac high 3 | Grid frequency high limit protect 3 |  |  |  | 0.01Hz
64 | Vac low C | Grid low voltage limit connect to Grid |  |  |  | 0.1V
65 | Vac high C | Grid high voltage limit connect to Grid |  |  |  | 0.1V
66 | Fac low C | Grid low frequency |  |  |  | 0.01
|  | limit connect to Grid |  |  |  | Hz
67 | Fac high C | Grid high frequency limit connect to Grid |  |  |  | 0.01 Hz
68 | Vac low1 time | Grid voltage low limit protect time 1 |  |  |  | Cycle
69 | Vac high1 time | Grid voltage high limit protect time 1 |  |  |  | Cycle
70 | Vac low2 time | Grid voltage low limit protect time 2 |  |  |  | Cycle
71 | Vac high2 time | Grid voltage high limit protect time 2 |  |  |  | Cycle
72 | Fac low1 time | Grid frequency low limit protect time 1 |  |  |  | Cycle
73 | Fac high1 time | Grid frequency high limit protect time 1 |  |  |  | Cycle
74 | Fac low2 time | Grid frequency low limit protect time 2 |  |  |  | Cycle
75 | Fac high2 time | Grid frequency high limit protect time 2 |  |  |  | Cycle
76 | Vac low3 time | Grid voltage low limit protect time 3 |  |  |  | Cycle
77 | Vac high3 time | Grid voltage high limit protect time 3 |  |  |  | Cycle
78 | Fac low3 time | Grid frequency low limit protect time 3 |  |  |  | Cycle
79 | Fac high3 time | Grid frequency high limit protect time 3 |  |  |  | Cycle
80 | U10min | Volt protection for 10 min |  |  |  | 0.1V |  | 1.1Vn
81 | PV Voltage High Fault | PV Voltage High Fault |  |  |  | 0.1V
82 | FW Build No. 5 | Model letter version number (TJ) |  |  |  | ASCII
83 | FW Build No. 4 | Model letter version number (AA) |  |  |  | ASCII
84 | FW Build No. 3 | DSP1 FW Build No. |  |  |  | ASCII
85 | FW Build No. 2 | DSP2/M0 FW Build No. |  |  |  | ASCII
86 | FW Build No. 1 | CPLD/AFCI FW Build No. |  |  |  | ASCII
87 | FW Build No. | M3 FW Build No. |  |  |  | ASCII
0
88 | ModbusVers ion | Modbus Version |  | Eg：207 is V2.07 |  | Int(16 bits)
89 | PFModel | Set PF function Model 0: PF=1 1: PF by set 2: default PF line 3: User PF line 4: UnderExcited (Inda) Reactive Power 5: OverExcited(Capa) Reactive Power 6：Q(v)model 7：Direct Control mode
8. Static capacitive QV mode 9. Static inductive QV mode
90 | GPRS IP Flag | Bit0-3:read:1;Set GPRS IP Successed Write:2;Read GPRS IP Successed Bit4-7:GPRS status |  | Bit0-3:ab out GPRS IP SET Bit4-7:ab out GRPRS Status
91 | FreqDerateS tart | Frequency derating start point |  |  |  | 0.01H Z
92 | FLrate | Frequency – load limit rate |  | 0-100 |  | 10tim es
93 | V1S | CEI021 V1S Q(v) |  | V1S<V2S |  | 0.1V
94 | V2S | CEI021 V2S Q(v) |  |  |  | 0.1V
95 | V1L | CEI021 V1L Q(v) |  | V1L<V1S |  | 0.1V
96 | V2L | CEI021 V2L Q(v) |  | V2L<V1L |  | 0.1V
97 | Qlockinpow er | Q(v) lock in active power of CEI021 |  | 0-100 |  | Percen t
98 | QlockOutpo wer | Q(v) lock Out active power of CEI021 |  | 0-100 |  | Percen t
99 | LIGridV | Lock in gird volt of CEI021 PF line |  | nVn |  | 0.1V
100 | LOGridV | Lock out gird volt of CEI021 PF line |  | nVn |  | 0.1V
101 | PFAdj1 | PF adjust value 1 |  | 4096 is 1
102 | PFAdj2 | PF adjust value 2 |  | 4096 is 1
103 | PFAdj3 | PF adjust value 3 |  | 4096 is 1
104 | PFAdj4 | PF adjust value 4 |  | 4096 is 1
105 | PFAdj5 | PF adjust value 5 |  | 4096 is 1
106 | PFAdj6 | PF adjust value 6 |  | 4096 is 1
107 | QVRPDelayTi meEE | QV Reactive Power delaytime |  | 0-30 |  | 1S |  | 3S
108 | OverFDeratD elayTimeEE | Overfrequency derati ngdelaytime |  | 0-20 |  | 50ms |  | 0
109 | QpercentMa x | Qmax for Q(V) curve |  | 0-1000 |  | 0.1%
110 | PFLineP1_LP | PF limit line point 1 load percent |  | 0-255 |  | percen t |  |  | 255 means no this point
111 | PFLineP1_PF | PF limit line point 1 power factor |  | 0-20000
112 | PFLineP2_LP | PF limit line point 2 load percent |  | 0-255 |  | percen t |  |  | 255 means no this point
113 | PFLineP2_PF | PF limit line point 2power factor |  | 0-20000
114 | PFLineP3_LP | PF limit line point 3 load percent |  | 0-255 |  | percen t |  |  | 255 means no this point
115 | PFLineP3_PF | PF limit line point 3 power factor |  | 0-20000
116 | PFLineP4_LP | PF limit line point 4 load percent |  | 0-255 |  | percen t |  |  | 255 means no this point
117 | PFLineP4_PF | PF limit line point 4 power factor |  | 0-20000
118 | Module 4 | Inverter Module (4) |  | &*11 |  |  |  |  | SxxBxx
119 | Module 3 | Inverter Module (3) |  | &*11 |  |  |  |  | DxxTxx
120 | Module 2 | Inverter Module (2) |  | &*11 |  |  |  |  | PxxUxx
121 | Module 1 | Inverter Module (1) |  | &*11 |  |  |  |  | Mxxxx Power
122 | ExportLimit_ En/dis | ExportLimit_En/dis |  | 1/0 |  |  |  |  | ExportLimit enable, 0: Disable exportLimit; 1: Enable 485 exportLimit; 2: Enable 232 exportLimit; 3: Enable CT exportLimit;
123 | ExportLimitP owerRate | ExportLimitPowerRate |  | -1000~+1 000 |  | 0.1% |  |  | ExportLimit PowerRate
124 | TrakerModel | Traker Model |  | 0,1,2 |  |  |  |  | 0:Independent 1:DC Source 2:Parallel
Second group
125 | INV Type-1 | Inverter type-1 |  |  |  | ASCII |  |  | Reserved
126 | INV Type-2 | Inverter type-2 |  |  |  | ASCII
127 | INV Type-3 | Inverter type-3 |  |  |  | ASCII
128 | INV Type-4 | Inverter type-4 |  |  |  | ASCII
129 | INV Type-5 | Inverter type-5 |  |  |  | ASCII
130 | INV Type-6 | Inverter type-6 |  |  |  | ASCII
131 | INV Type-7 | Inverter type-7 |  |  |  | ASCII
132 | INV Type-8 | Inverter type-8 |  |  |  | ASCII
133 | BLVersion1 | Boot loader version1 | [6 empty] | Reserved
134 | BLVersion2 | Boot loader version2 | [6 empty] | Reserved
135 | BLVersion3 | Boot loader version3 | [6 empty] | Reserved
136 | BLVersion4 | Boot loader version4 | [6 empty] | Reserved
137 | Reactive P ValueH | Reactive PowerH |  |  |  | 0.1var
138 | Reactive P ValueL | Reactive PowerL |  |  |  | 0.1var
139 | ReactiveOut putPriorityE nable | ReactiveOutput Priority Enable |  |  |  | 0/1 |  |  | 0：disable 1：enable
140 | Reactive P Value(Ratio) | Reactive Power Ratio |  |  |  | 0.1
……
141 | SvgFunction Enable | Svg enable on night |  |  |  | 0/1 |  |  | 0：disable 1：enable
142 | uwUnderFU ploadPoint | UnderF Upload Point |  |  |  | 0.01H Z
143 | uwOFDerate RecoverPoin t | OFDerate RecoverPoint |  |  |  | 0.01H Z
144 | uwOFDerate RecoverDela yTime | OFDerate RecoverDelayTime |  | 0-30000 |  | 50ms
145 | ZeroCurrent Enable | ZeroCurrent Enable |  | 0-1
146 | uwZeroCurre ntStaticlowV olt | ZeroCurrent StaticlowVolt |  | 46-230V |  | 0.1V |  | 115V
147 | uwZeroCurre ntStaticHigh Volt | ZeroCurrent StaticHighVolt |  | 230-276V |  | 0.1V |  | 276V
148 | uwHVoltDer | HVoltDerate HighPoint |  | 0-1000V |  | 0.1V
ateHighPoint
149 | uwHVoltDer ateLowPoint | HVoltDerate LowPoint |  | 0-1000V |  | 0.1V
150 | uwQVPower StableTime | QVPower Stable Time |  | 0-60S |  | 0.1S
151 | uwUnderFU ploadStopPo int | UnderF Upload StopPoint |  |  |  | 0.01H Z
152 | fUnderFreqP oint | Underfrequency load start point |  | 46.00-50. 00 |  | 0.01Hz |  | 49.8 | CEI
153 | fUnderFreqE ndPoint | Underfrequency down load end point |  | 46.00-50. 00 |  | 0.01Hz |  | 49.1 | CEI
154 | fOverFreqPo int | Over frequency loading start point |  | 50.00-52. 00 |  | 0.01Hz |  | 50.2 | CEI
155 | fOverFreqEn dPoint | Over frequency loading end point |  | 50.00-52. 00 |  | 0.01Hz |  | 51.5 | CEI
156 | fUnderVoltP oint | Undervoltage load shedding start point |  | 160-300 |  | 0.1V |  | 220 | CEI
157 | fUnderVoltE ndPoint | Undervoltage derating end point |  | 160-300 |  | 0.1V |  | 207 | CEI
158 | fOverVoltPoi nt | Overvoltage loading start point |  | 160-300 |  | 0.1V |  | 230 | CEI
159 | fOverVoltEn dPoint | Overvoltage loading end point |  | 160-300 |  | 0.1V |  | 245 | CEI
160 | uwNominal GridVolt | NominalGridVolt Select |  | 0~3 |  |  |  |  | UL
161 | uwGridWatt Delay | GridWatt DelayTime |  | 0~3000 |  | 20ms |  |  | UL
162 | uwReconnec tStartSlope | Reconnect StartSlope |  | 1~1000 |  | 0.1 |  |  | UL
163 | uwLFRTEE | LFRT1 Freq |  | 5500~650 0 |  | 0.01Hz |  |  | UL
164 | uwLFRTTime EE | LFRT1 Time |  |  |  | 20ms |  |  | UL
165 | uwLFRT2EE | LFRT2 Freq |  | 5500~650 0 |  | 0.01Hz |  |  | UL
166 | uwLFRTTime 2EE | LFRT2 Time |  |  |  | 20ms |  |  | UL
167 | uwHFRTEE | HFRT1 Freq |  | 5500~650 0 |  | 0.01Hz |  |  | UL
168 | uwHFRTTim eEE | HFRT1 Time |  |  |  | 20ms |  |  | UL
169 | uwHFRT2EE | HFRT2 Freq |  | 5500~650 0 |  | 0.01Hz |  |  | UL
170 | uwHFRTTim e2EE | HFRT2 Time |  |  |  | 20ms |  |  | UL
171 | uwHVRTEE | HVRT1 Volt |  |  |  | 0.001 Un |  |  | UL
172 | uwHVRTTim eEE | HVRT1 Time |  |  |  | 20ms |  |  | UL
173 | uwHVRT2EE | HVRT2 Volt |  |  |  | 0.001 Un |  |  | UL
174 | uwHVRTTim e2EE | HVRT2 Time |  |  |  | 0.001 Un |  |  | UL
175 | uwUnderFU ploadDelayTi me | UnderF UploadDelayTime |  | 0-2s |  | 50ms |  | 0s | 50549
176 | uwUnderFU ploadRateEE | UnderF UploadRate | [6 empty] | 50549
177 | uwGridResta rt_H_Freq | GridRestart HighFreq |  |  |  | 0.01Hz |  |  | 50549
178 | OverFDeratR esponseTim e | OverFDerat ResponseTime |  | 0-500
179 | UnderFUplo adResponse Time | UnderFUpload ResponseTime |  | 0-500
Intelligent control reads relevant data, used to identify the logo 180-200
180 | MeterLink | Whether to elect the meter | [6 empty] | 0: Missed, 1: Received
181 | OPT Number | Number of connection optimizers |  | 0-64 |  |  |  |  | The total number of optimizers connected to the inverter
182 | OPT ConfigOK Flag | Optimizer configuration completion flag | [6 empty] | 0x00:Not configured success 0x01:Configuration is complete
183 | PvStrScan | String Num |  | 0、8、16、 32 |  |  |  |  | 0：Not support Other：PvString Num
184 | BDCLinkNum | BDC parallel Num | [6 empty] | The number of BDCs connected to the current machine Default is 0
185 | PackNum | Number of battery modules | [6 empty] | Total number of battery modules currently associated with all BDCs
186 | Reserved
187 | VPP function enable status | VPP function enable status | [6 empty] | 0：Disable 1：Enable
188 | dataLog Connect Server status | dataLog Connect Server status | [6 empty] | 0：connection succeeded 1：Connection failed
……
200 | Reserved | [7 empty] | Reserved
201 | PID Working Model | PID Operating mode |  | 0: automati c 1: continuo us 2: All night
202 | PID On/Off Ctrl | PID Break control |  | 0:On 1:Off
203 | PID Volt Option | PID Output voltage option |  | 300~1000 |  | V
…… | [8 empty] | Reserved
209 | New Serial NO | Serial number 1-2 |  |  |  | ASCII
210 | New Serial NO | Serial number 3-4 |  |  |  | ASCII
211 | New Serial NO | Serial number 5-6 |  |  |  | ASCII
212 | New Serial NO | Serial number 7-8 |  |  |  | ASCII
213 | New Serial NO | Serial number 9-10 |  |  |  | ASCII
214 | New Serial NO | Serial number 11-12 |  |  |  | ASCII
215 | New Serial NO | Serial number 13-14 |  |  |  | ASCII
216 | New Serial | Serial number 15-16 |  |  |  | ASCII
217 | New Serial | Serial number 17-18 |  |  |  | ASCII
218 | New Serial | Serial number 19-20 |  |  |  | ASCII
219 | New Serial | Serial number 21-22 |  |  |  | ASCII
220 | New Serial | Serial number 23-24 |  |  |  | ASCII
221 | New Serial | Serial number 25-26 |  |  |  | ASCII
222 | New Serial | Serial number 27-28 |  |  |  | ASCII
223 | New Serial | Serial number 29-30 |  |  |  | ASCII
…… | [8 empty] | Reserved
229 | EnergyAdjus t | Power generation incremental calibration coefficient |  |  |  | 0.1% |  |  | 1-1000,(Percent ratio)
230~249 for growatt debug setting
230 | IslandDisabl e | Island Disable or not. 1:disable 0:Enable |  | 0,1 |  |  |  | 0
231 | FanCheck | Start Fan Check |  | 1
232 | EnableNLine | Enable N Line of grid |  | 1 |  |  |  | 0
233 | wCheckHard ware | wCheckHardware Bit0: GFCIBreak; Bit1:SPSDamage Bit8:EepromReadWarni ng Bit9:EEWriteWarning ……
234 | wCheckHard ware2 | [7 empty] | reserved
235 | ubNToGNDD etect | Dis/enable N to GND detect function |  | 1:enable 0:disable |  |  |  | 1
236 | NonStdVacE nable | Enable/Disable Nonstandard Grid voltage range |  | 0-2 |  |  |  | 0 | 0:Disable; 1:Enable Voltgrade1 2:Enable Voltgrade2
237 | uwEnableSp ecSet | Disablse/enable appointed spec setting |  | 1:enable 0:disable |  | Binary |  | 0x000 0 | Bit 0: Hungary
238 | Fast MPPT enable | About Fast mppt |  | 0,1,2 |  |  |  | 0 | Reserved
239 | / | / |  | / |  |  |  | / | Reserved
240 | Check Step
241 | INV-Lng | Inverter Longitude | [6 empty] | Longitude
242 | INV-Lat | Inverter Latitude | [6 empty] | Latitude
…… | [8 empty] | Reserved
303 | [8 empty] | Reserved
304 | uwAntiBackf lowFailPowe rLimitEE | Anti-backflow failure power percentage |  | 0-1000 |  | 0.1% |  |  | Anti-backflow failure default setting power percentage
305 | Qloadspeed | Reactive loading speed |  | 0-100 |  | 1% |  |  | Reactive power adjustment speed setting item, n%Pn/s, 0 means that the loading speed is not enabled, that is, it is directly loaded to the set value
306 | bParallelAnti BackflowEna ble | ParallelAnti-Backflow Enable |  | 0-1 |  |  |  |  | Parallel anti-Backflow open enable bit 1: enable 0:disable
307 | uwAntiBackf lowFailureRe sponseTime | AntiBackflowFailure ResponseTime |  | 1-5000 |  | 1s |  |  | AntiBackflow Failure Response Time
308 | uwParallelAn tiBackflowPo werLimitEE | ParallelAntiBackflowPo wer |  | 0-1000 |  | 0.1% |  |  | Parallel AntiBackflow Power
limit value setting
309 | bISOCheckC md | ISO detection command |  | 0-1 |  | 1 |  |  | ISO detection command
310 | bGPRSStatus | GPRS Status 1: module not working 2: no sim card 3: No internet 4. TCP not connecting to server 5. TCP connection succeeded |  | 0-255 |  | 1
311 | uwQmax_In ductive | The inductive Qmax of the Q(V) curve |  | 0-1000 |  | 0.1%
312 | uwQmax_Ca | The Capactive Qmax of |  | 0-1000 |  | 0.1%
| pactive | the Q(V) curve
313 | uwReactiveP owerAdjustF ailureRespon seTime | ReactivePowerAdjust Failur ResponseTime |  | 0-5000 |  | S
314 | bSuperAntiB ackflowEnab le | SuperAntiBackflow Enable | [6 empty] | 0：disable，1：enable
315 | uwReactiveP owerStableT ime | ReactivePowerStableTi me |  | 0-200 |  | S
316 | uwQpStable Time | QpStableTime |  | 0-200 |  | S
317 | uwPuDerate Time | PuDerateTime |  | 0-200 |  | S
318 | uwQVModel Q2Point | QV mode Q2 set point reactive power percentage |  | 0-2000 |  | 0.1% |  |  | Capacitive 30% （ The corresponding setting is 700)； Inductive 30% (The corresponding setting is 1300)； used for IEE1547
319 | uwQVModel Q3Point | QV mode Q3 set point reactive power percentage |  | 0-2000 |  | 0.1%
320 | bVrefModel Enable | VrefModelEnable |  | 0 ： Vref mode for QV curve is not active 1 ： Vref mode for QV curve is active |  |  |  |  | When the Vref mode is not activated, the V1~V4 and Q1~Q4 upper computer of the QV curve can be adjusted; When Vref mode is activated, V1~V4 of the QV curve are determined with Vref and cannot be changed, and Q1~Q4 can be modified by the host computer .used for IEE1547
321 | uwVrefMod elFilterTime | VrefModelFilterTime |  | 0-5000 |  | S |  |  | Activate Vref mode, the output filter value is equal to Vref with in the set time .used for IEE1547
322 | uwUserQPM odeP1Krate | Active power P1 set point percentage for QP mode |  | 0-1000 |  | 0.1% |  |  | used for IEE1547
323 | uwUserQPM odeP2Krate | Active power P2 set point percentage for QP mode |  | 0-1000 |  | 0.1% |  |  | used for IEE1547
324 | uwUserQPM odeP3Krate | Active power P3 set point percentage for QP mode |  | 0-1000 |  | 0.1% |  |  | used for IEE1547
325 | uwUserQPM odeQ1Krate | Reactive power Q1 set point percentage for QP mode |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
326 | uwUserQPM odeQ2Krate | Reactive power Q2 set point percentage for QP mode |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
327 | uwUserQPM odeQ3Krate | Reactive power Q3 set point percentage for QP mode |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
328 | uwAcVoltHig hDeratPowe rLimit | AcVoltHighDeratPower Limit |  | 0-1000 |  | 0.1%
329 | BackflowSin gleCtrl | BackflowSingleCtrl |  | 0: disable 1: enable
330 | bAntiBackflo wProtectMo de | AntiBackflowProtectM ode |  | 0-3 |  |  |  |  | Used for Australian
331 | uwUnderFU ploadZeroPo werPoint | UnderfreqUploadZeroP owerPoint |  |  |  | 0.01H Z
332 | FreqDerateZ eroPowerPoi nt | FreqDerateZeroPowerP oint |  |  |  | 0.01H Z
333 | bFreqDerati ngStopMode Enable | FreqDeratingStopMode Enable |  | 0-1
334 | bFreqIncreas ingEnable | FreqIncreasingEnable |  | 0-1
335 | uwFreqIncre asingRecove rTime | FreqIncreasingRecover Time |  |  |  | 50ms
336 | uwFreqIncre asingEndLow | FreqIncreasingEndLow Point |  |  |  | 0.01H Z
Point
337 | bFreqIncreas ingStopMod eEnable | FreqIncreasingStopMo deEnable |  | 0-1
338 | uwUserQpC hrP1Krate | User QP function, charge P1 set point percentage |  | 0-1000 |  | 0.1%
339 | uwUserQpC hrP2Krate | User QP function, charge P2 set point percentage |  | 0-1000 |  | 0.1%
340 | uwUserQpC hrP3Krate | User QP function, charge P3 set point percentage |  | 0-1000 |  | 0.1%
341 | wUserQpChr Q1Krate | User QP function, charge Q1 set point percentage |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
342 | wUserQpChr Q2Krate | User QP function, charge Q2 set point percentage |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
343 | wUserQpChr Q3Krate | User QP function, charge Q3 set point percentage |  | -1000-10 00 |  | 0.1% |  |  | -1000~1000：Inductive（100%） ~ Capacitive（100%）
344 | uwFreqDerat ingRecoverL owPoint | FreqDeratingRecoverLo wPoint |  |  |  | 0.01H Z
345 | uwFreqIncre asingRecove rHighPoint | FreqIncreasingRecover HighPoint |  |  |  | 0.01H Z
…….
532 | TurnOffUnlo adSpeed | TurnOffUnloadSpeed |  | 0-1000 |  |  |  | 0.1% | 0 means not enabled, that is, the function is not enabled; 1-1000 means n%Pn/min
533 | LimitDevice | Anti-backflow equipment selection |  | 0-3 |  |  |  |  | 1：Meter 3:CT
other meaningless
534 | PowerSetOn DCSourceMo de | Power settings in dc source mode |  | 0-90000 |  |  |  |  | The unit is W
535 | OUFreqGrad e1En | Over-under-frequency |  | 0-1 |  |  |  |  | 0:disable 1:enable
Grade1Enable,
currently only used by
CEI0-21
536 | Country Set | Country settings under the same safety regulations |  | 0-200 |  |  |  |  | For mobile APP use only
538 | InterlockEna ble | Three-machine communication Interlock function mode |  | 0-2 |  |  |  |  | 0：disable
1: Slave Enable 2. host enable
539 | OvTemperDe ratePoint | Over temperature derate point
540 | SafetySetPas sword | Switch between different safety regulations to set the password
541 | AFCI Onoff | AFCI Onoff |  | 0xA0/0xA 5 |  |  |  |  | 0xA0：AFCI off 0xA5：AFCI on
542 | AfciSelfChec k | AfciSelfCheck | [6 empty] | 0：No self check 1: self check
543 | AfciReset | AfciReset | [6 empty] | 0：Not Reset 1: Reset
544 | AFCIValue1 | AFCIThresholdValue （low） |  | 0-65000
545 | AFCIValue2 | AFCIThresholdValue （middle） |  | 0-65000
546 | AFCIValue3 | AFCIThresholdValue （High） |  | 0-65000
547 | OverThresho ldValueMaxC nt | OverThresholdValueMa xCnt |  | 0-255
548 | AFCIScanTyp eEnable | AFCI curve scan type |  | 1~4 |  |  |  |  | 1：A road strength
2：A road FFT value 3：B road strength 4：B road FFT value
549 | PowerVoltSt opModeEn | PowerVoltStopModeEn |  | 0、1 |  |  |  |  | 0：disable 1:enable
The power is restored when the voltage is less than the recovery point
550 | VoltWattRec overTime | Voltage active power recovery time |  | 0-15000 |  | 20ms
551 | HVoltDerate | Voltage active cut-off |  | -5000-11
| StopPower | power |  | 400
552 | QVTimeExpo nent | QVTimeExponent |  | 1-255 |  |  |  |  | Q varies exponentially with time
553 | Volt-Watt Watt1 | Voltage active V1 point, corresponding active power |  | 0-11400
554 | Volt-Watt Watt2 | Voltage active V2 point, corresponding active power |  | 0-11400
……
600 | Volt-Var Var1 | Voltage reactive V1 point, Corresponding reactive power percentage(Capacitive |  | 0-1000 |  |  |  |  | 0%~100.0%,US latest safety regulations
Qmax)
601 | Volt-Var Var2 | Voltage reactive V2 point, Corresponding reactive power percentage |  | 0-1000 |  |  |  |  | 0%~100.0%,US latest safety regulations
602 | Volt-Var Var3 | Voltage reactive V3 point, Corresponding reactive power percentage |  | 0-1000 |  |  |  |  | 0%~100.0%,US latest safety regulations
603 | Volt-Var Var4 | Voltage reactive V4 point, Corresponding reactive power percentage(Inductive Qmax) |  | 0-1000 |  |  |  |  | 0%~100.0%,US latest safety regulations
604
605 | OPModEner gize | Allowed inverter output power |  | 0/1 |  |  |  |  | 0: output power not allowed 1: allowable output power For US models
608 | OneKeySetB DCMode | One key to set battery mode function | [6 empty] | 0: self-use 1: battery priority 2: Grid priority 255：Disable Currently used for US models
609 | PowerOutpu tEnable | Zero Power Output Enable | [6 empty] | 0：Zero Power Output
1：Unlimited output power (default is 1)
610 | DealDebugP araFlag | Flag bit for clearing debug variables | [6 empty] | Currently only bit0 and bit1 are used bit0 is used to manually clear the Debug data uploaded to the server bit1 is used to manually clear the fault codes that need to be powered off to clear
612 | bAcCoupleE n | AcCoupleEn |  | 0-1 |  |  |  |  | 0：disable 1：enable
…..
660 | ReloadCmd | M3 remote command | [6 empty] | 0xA0: Initialize safety defaults 0xAA: Reboot M3 remotely
Six group for Storage Power
Register NO. | Variable Name | Description |  | Value |  | Unit |  | Initial value | Note
1000 | Float charge current limit | When charge current battery need is lower than this value, enter into float charge |  |  |  | 0.1A |  | 600 | CC current
1001 | PF CMD memory state | Set the following 19-22 CMD will be memory ornot(1/0), if not, these settings are the initial value. |  | 0or1, |  |  |  | 0 | Means these settings will be acting or not when next power on(02 repeat)
1002 | VbatStartF orDischarg e | LV Vbat |  |  |  | 0.1V |  |  | Lead-acid battery LV voltage
1003 | VbatlowWa rnClr | LoadPercent(only lead-Acid): 45.5V <20% 48.0V 20%~50% 49.0V >50 |  |  |  | 0.1V |  |  | Clear battery low voltage error voltage point
1004 | Vbatstopfo rdischarge | Should stop discharge when lower than this |  |  |  | 0.01V
voltage(only lead-Acid): 46.0V <20% 44.8V 20%~50% 44.2V >50%
1005 | Vbat stop for charge | Should stop charge when higher than this voltage |  |  |  | 0.01V |  | 5800
1006 | Vbat start for discharge | Should not discharge when lower than this voltage |  |  |  | 0.01V |  | 4800
1007 | Vbat constant charge | can charge when lower than this voltage |  |  |  | 0.01V |  | 5800 | CV voltage（acid）
1008 | EESysInfo.S ysSetEn | Bit0：Resved; Bit1：Resved; Bit2：Resved; Bit3：Resved; Bit4：Resved; Bit5：bDischargeEn； Bit6：ForceDischrEn； Bit7：ChargeEn； Bit8：bForceChrEn； Bit9：bBackUpEn； Bit10：bInvLimitLoadE； Bit11：bSpLimitLoadEn； Bit12：bACChargeEn； Bit13：bPVLoadLimitEn; Bit14,15:UnUsed; | [6 empty] | System Enable
1009 | Battemp lower limit d | Battery temperature lower limit for discharge |  | 0-200:0-2 0℃ 1000-140 0：-40-0℃ |  | 0.1℃ |  | 1170
1010 | Bat temp upper limit d | Battery temperature upper limit for discharge |  | 200-1000 |  | 0.1℃ |  | 420
1011 | Bat temp lower limit c | Battery temperature lower limit for charge |  | 0-200:0-2 0℃ 1000-140 0：-40-0℃ |  | 0.1℃ |  | 30 | Lower temperature limit
1012 | Bat temp upper limit c | Battery temperature upper limit for charge |  | 200-1000 |  | 0.1℃ |  | 370 | Upper temperature limit
1013 | uwUnderFr eDischarge DelyTime | Under Fre Delay Time |  | 0-20 |  | 50ms |  |  | Under Fre Delay Time
1014 | BatMdlSeri alNum | Battery serial number |  | 00:00 |  |  |  |  | SPH4-11K used
1015 | BatMdlPara llNum | Battery parallel section |  | 00:00 |  |  |  |  | SPH4-11K used
1016 | DRMS_EN | / |  | / |  | / |  | / | 0：disable 1：enable
1017 | Bat First Start Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59
1018 | Bat First Stop Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59
1019 | BatFirst on/off Switch 4 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Battery priority enable 1
1020 | Bat First Start Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59
1021 | Bat First Stop Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59
1022 | BatFirst on/off Switch 5 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Battery priority enable 1
1023 | Bat First Start Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59
1024 | Bat First Stop Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59
1025 | BatFirst on/off Switch 6 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Battery priority enable 1
1026 | Grid First Start Time | High eight:hours Low eight: minutes |  | 0-23 0-59
4
1027 | Grid First Stop Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59
1028 | Grid First Stop Switch 4 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Grid priority enable
1029 | Grid First Start Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59
1030 | Grid First Stop Time 5 | High eight:hours Low eight: minutes |  | 0-23 0-59
1031 | Grid First Stop Switch 5 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Grid priority enable
1032 | Grid First Start Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59
1033 | Grid First Stop Time 6 | High eight:hours Low eight: minutes |  | 0-23 0-59
1034 | Grid First Stop Switch 6 | Enable:1 Disable:0 |  | 0 or 1 |  |  |  |  | Grid priority enable
1035 | Bat First Start Time 4 | High eight:hours Low eight: minutes |  | 0-23 0-59
1036 | / | / |  | / |  | / |  | / | Reserve
1037 | bCTMode | Use the CTMode to Choose RFCT \ Cable CT\METER |  | 2:METER 1:cWirele ssCT 0:cWiredC T |  |  |  | 0
1038 | CTAdjust | CTAdjust enable |  | 0:disable 1:enable |  |  |  | 0
1039 | / | / |  | / |  | / |  | / | Reserve
1040 | / | / |  | / |  | / |  | / | Reserve
1041 | / | / |  | / |  | / |  | / | Reserve
1042 | / | / |  | / |  | / |  |  | Reserve
1043 | / | / |  | / |  | / |  | / | Reserve
1044 | Priority | ForceChrEn/ForceDischr En Load first/bat first /grid first |  | 0.Load(de fault)/1.B attery/2.G rid |  |  |  |  | bForceChrEn/disbForceDischrE n/dis
1045 | / | / |  | / |  | / |  | / | Reserve
1046 | / | / |  | / |  | / |  | / | Reserve
1047 | AgingTestSt ep Cmd | Command for aging test |  | 0: default 1: charge 2: discharge |  |  |  |  | Cmd for aging test
1048 | BatteryTyp e | Battery type choose of buck-boost input |  | 0:Lithium 1:Lead-aci d 2:other |  |  |  | 0 | Battery type
1049 | / | / |  | / |  | / |  |  | Reserve
1050 | / | / |  | / |  | / |  | / | Reserve
1051 | / | / |  | / |  | / |  |  | Reserve
1052 | / | / |  | / |  | / |  |  | Reserve
1053 | / | / |  | / |  | / |  |  | Reserve
1054 | / | / |  | / |  | / |  | / | Reserve
1060 | BuckUpsFunE n |  | Ups function enable or disable |  | 0:disable 1:enable
1061 | BuckUPSVoltS et |  | UPS output voltage |  | 0:230 1:208 2:240 |  |  |  | 230V
1062 | UPSFreqSet |  | UPS output frequency |  | 0:50Hz 1:60Hz |  |  |  | 50Hz
... | / |  | / | / | / |  | / |  | / | reverse
Priority set
1070 | GridFirstDisch argePowerRat e |  | Discharge Power Rate when Grid First | W | 0-100 |  | 1% |  | Discharge Power Rate when Grid First
1071 | GridFirstStopS OC |  | Stop Discharge soc when Grid First | W | 0-100 |  | 1% |  | Stop Discharge soc when Grid First
1072… 1079 | / |  | / | / | / |  | / |  | / |  | reverse
1080 | Grid First Start Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1081 | Grid First Stop Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1082 | Grid First Stop Switch 1 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Grid First enable
1083 | Grid First Start Time 2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1084 | Grid First Stop Time 2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1085 | Grid First Stop Switch 2 |  | ForceDischarge.bSwitch&L CD_SET_FORCE_TRUE_2)= =LCD_SET_FORCE_TRUE_2 |  | 0 or 1 |  |  |  | Grid First enable |  | ForceDischarge; LCD_SET_FORCE_T RUE_2
1086 | Grid First Start Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1087 | Grid First Stop Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1088 | Grid First Stop Switch 3 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Grid First enable
1089 | / |  | / | / | / |  | / |  | / |  | reserve
1090 | BatFirstPower Rate |  | Charge Power Rate when Bat First | W | 0-100 |  | 1% |  | Charge Power Rate when Bat First
1091 | wBatFirst stop SOC |  | Stop Charge soc when Bat First | W | 0-100 |  | 1% |  | Stop Charge soc when Bat First
1092 | AC charge Switch |  | When Bat First Enable:1 Disable:0 |  | Enable:1 Disable:0 |  |  |  | AC Charge Enable
1093… 1099
1100 | Bat First Start Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1101 | Bat First Stop Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1102 | BatFirst on/off Switch 1 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Bat First Enable1
1103 | Bat First Start Time 2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1104 | Bat First Stop Time 2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1105 | BatFirston/off Switch 2 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Bat First Enable2
1106 | Bat First Start Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1107 | Bat First Stop Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59
1108 | BatFirston/off Switch 3 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Bat First Enable3
1109 | / |  | / | / | / |  | / |  | / |  | reserve
1110 | Load First Start Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1111 | Load First Stop Time 1 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1112 | Load First Switch 1 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Load First Enable |  | SPA/ reserve
1113 | Load First Start Time2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1114 | Load First Stop Time 2 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1115 | Load First Switch 2 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Load First Enable |  | SPA/ reserve
1116 | Load First Start Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1117 | Load First Stop Time 3 |  | High eight bit：hour Low eight bit：minute |  | 0-23 0-59 | [5 empty] | SPA/ reserve
1118 | Load First Switch 3 |  | Enable :1 Disable:0 |  | 0 or 1 |  |  |  | Load First Enable |  | SPA/ reserve
1119 | NewEPowerC alcFlag |  | / | / | / |  | / |  | / |  | 0：The old formula 1 ： The new formula
1120 | BackUpEn |  | BackUp Enable | [7 empty] | MIX US
1121 | SGIPEn |  | SGIP Enable | [7 empty] | MIX US
……… | 1122~1124 |  | / | / | / |  | / |  | / |  | reserve
1125 | BatSerialNO. 8 |  | Product serial number of the first PACK of energy storage batteries | / | / |  | ASCII
1126 | BatSerialNO. 7 |  |  | / | / |  | ASCII
1127 | BatSerialNO. 6 |  |  | / | / |  | ASCII
1128 | BatSerialNO. 5 |  |  | / | / |  | ASCII
1129 | BatSerialNO. 4 |  |  | / | / |  | ASCII
1130 | BatSerialNO. 3 |  |  | / | / |  | ASCII
1131 | BatSerialNO. 2 |  |  | / | / |  | ASCII
1132 | BatSerialNO. 1 |  |  | / | / |  | ASCII
1132 ~1204 | BatSerialNO. 8~ BatSerialNO. 1 |  | The serial number of the second to tenth packs of the energy storage battery consists of nine packs, and | / | / |  | ASCII
the format of the serial number of each PACK is 1125 to 1132
……
1244 | Com version NameH |  | Name of the battery main control firmware version |  |  |  | ASCII
1245 | Com version NameL |  | Name of the battery main control firmware version |  |  |  | ASCII
1246 | Com version No |  | Version of the battery main control firmware |  |  |  | digital
1247 | Com version NameH |  | Name of battery monitoring firmware version |  |  |  | ASCII
1248 | Com version NameL |  | Name of battery monitoring firmware version |  |  |  | ASCII
1249 | Com version No |  | Battery monitoring firmware version |  |  |  | digital
Use for TL-X and TL-XH
3000 | ExportLimitFa iledPowerRat e |  | The power rate when exportLimit failed | R/W |  |  | 0.1% |  |  |  | The power rate when exportLimit failed
3001 | New Serial NO |  | Serial number 1-2 | R/W |  |  | ASCII |  |  |  | The new model uses the following registers to record the serial number; The representation is the same as the original: one register holds two characters and the new serial number is 30 characters.
3002 | New Serial NO |  | Serial number 3-4 | R/W |  |  | ASCII
3003 | New Serial NO |  | Serial number 5-6 | R/W |  |  | ASCII
3004 | New Serial NO |  | Serial number 7-8 | R/W |  |  | ASCII
3005 | New Serial NO |  | Serial number 9-10 | R/W |  |  | ASCII
3006 | New Serial NO |  | Serial number 11-12 | R/W |  |  | ASCII
3007 | New Serial NO |  | Serial number 13-14 | R/W |  |  | ASCII
3008 | New Serial NO |  | Serial number 15-16 | R/W |  |  | ASCII
3009 | New Serial NO |  | Serial number 17-18 | R/W |  |  | ASCII
3010 | New Serial NO |  | Serial number 19-20 | R/W |  |  | ASCII
3011 | New Serial NO |  | Serial number 21-22 | R/W |  |  | ASCII
3012 | New Serial NO |  | Serial number 23-24 | R/W |  |  | ASCII
3013 | New Serial NO |  | Serial number 25-26 | R/W |  |  | ASCII
3014 | New Serial NO |  | Serial number 27-28 | R/W |  |  | ASCII
3015 | New Serial NO |  | Serial number 29-30 | R/W |  |  | ASCII
3016 | DryContactFu ncEn |  | DryContact function enable | R/W | 0:Disable 1: Enable | [5 empty] | DryContact function enable
3017 | DryContactOn Rate |  | The power rate of drycontact turn on | R/W | 0~1000 |  | 0.1% |  |  |  | The power rate of drycontact turn on
3018 | bWorkMode |  | WorkMode 0:default,1: System Retrofit 2: Multi-Parallel | R/W | 0、1、2 | [5 empty] | MIN2.5~6KTL-XH/ XA Double CT special
3019 | DryContactOf fRate |  | DryContactOffRate | Dry contact closure power | R/W |  | 0~100 0 |  | 0.1% |  | Dry contact closure power pe rcentage
3020 | BoxCtrlInvOrd er |  | BoxCtrlInvOrder | Off-net box control instruct ion | R/W
3021 | ExterCommOf fGridEn |  | External communication setting manual off-network enable | R/W | [6 empty] | 0x00: Disable; （default） 0x01: Enable;
3022 | uwBdcStopW orkOfBusVolt |  | BdcStopWorkOfBusVolt | R
3023 | bGridType |  | GridType---0:SinglePhase 1:ThreePhase 2:SplitPhase | R/W | 0、1、2 | [5 empty] | MIN2.5~6KTL-XH/ XA Double CT special
3024 | Float charge current limit |  | When charge current battery need is lower than | R/W |  |  | 0.1A |  | 600 |  | CC current
this value, enter into float charge
3025 | VbatWarning |  | "Battery-low" warning setup voltage | R/W |  |  | 0.1V |  | 4800 |  | Lead acid battery LV voltage
3026 | VbatlowWarn Clr |  | "Battery-low" warning clear voltage | R/W |  |  | 0.1V |  |  |  | Clear battery low voltage error voltage point LoadPercent(only lead-Acid): 45.5V(Load < 20%); 48.0V(20%<=Load <=50%); 49.0V(Load > 50%);
3027 | Vbatstopfordi scharge |  | Battery cut off voltage | R/W |  |  | 0.1V |  |  |  | Should stop discharge when lower than this voltage(only lead-Acid): 46.0V(Load < 20%); 44.8V(20%<=Load <=50%); 44.2V(Load > 50%);
3028 | Vbat stop for charge |  | Battery over charge voltage | R/W |  |  | 0.01V |  | 5800 |  | Should stop charge when higher than this voltage
3029 | Vbat start for discharge |  | Battery start discharge voltage | R/W |  |  | 0.01V |  | 4800 |  | Should not discharge when lower than this voltage
3030 | Vbat constant charge |  | Battery constant charge voltage | R/W |  |  | 0.01V |  | 5800 |  | CV voltage（acid） can charge when lower than this voltage
3031 | Battemp lower limit d |  | Battery temperature lower limit for discharge | R/W |  |  | 0.1℃ |  | 1170 |  | 0-200:0-20℃ 1000-1400： -40-0℃
3032 | Bat temp upper limit d |  | Battery temperature upper limit for discharge | R/W |  |  | 0.1℃ |  | 420
3033 | Bat temp lower limit c |  | Battery temperature lower limit for charge | R/W |  |  | 0.1℃ |  | 30 |  | Battery temperature lower limit 0-200:0-20℃ 1000-1400： -40-0℃
3034 | Bat temp upper limit c |  | Battery temperature upper limit for charge | R/W |  |  | 0.1℃ |  | 370 |  | Battery temperature upper limit
3035 | uwUnderFreD ischargeDelyT ime |  | Under Fre Delay Time | R/W |  |  | 50ms |  |  |  | Under Fre Delay Time
3036 | GridFirstDisch argePowerRat e |  | Discharge Power Rate when Grid First | [5 empty] | 1-255
3037 | GridFirstStopS OC |  | Stop Discharge soc when Grid First | [5 empty] | 1-100
3038 | Time 1(xh) |  | Period 1: [Start Time ~ End Time], [Charge/Discharge], [Disable/Enable] 3038 enable, charge and discharge, start time, end time 3039 | R/W | [6 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1: enabled;
3039 |  |  |  | R/W | [6 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3040 | Time 2(xh) |  | Time period 2: [start time ~ end time], [charge / discharge], [disable / enable] 3040 enable, charge and discharge, start time, 3041 end time | R/W | [6 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~14, 0: load priority; 1: battery priority; 2: Grid priority; Bit15, 0: prohibited; 1:
enabled;
3041 |  |  |  | R/W | [6 empty] | Bit0~7: minutes; Bit8~12: hour; Bit13~15: reserved
3042 | Time 3(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3043 |  |  |  | R/W | [6 empty] | With Time1
3044 | Time 4(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3045 |  |  |  | R/W | [6 empty] | With Time1
3046 | 预留
3047 | BatFirstPower Rate |  | Charge Power Rate when Bat First | [5 empty] | 1-100
3048 | wBatFirst stop SOC |  | Stop Charge soc when Bat First | [5 empty] | 1-100
3049 | AcChargeEna ble |  | AcChargeEnable | [7 empty] | Enable :1 Disable:0
3050 | Time 5(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3051 |  |  |  | R/W | [6 empty] | With Time1
3052 | Time 6(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3053 |  |  |  | R/W | [6 empty] | With Time1
3054 | Time 7(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3055 |  |  |  | R/W | [6 empty] | With Time1
3056 | Time 8(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3057 |  |  |  | R/W | [6 empty] | With Time1
3058 | Time 9(xh) |  | With Time1 | R/W | [6 empty] | With Time1
3059 |  |  |  | R/W | [6 empty] | With Time1
3060~ 3069 | Reserved
3070 | BatteryType |  | Battery type choose of buck-boost input | R/W | [6 empty] | Battery type 0:Lithium 1:Lead-acid 2:other
3071 | BatMdlSeria/ ParalNum |  | BatMdlSeria/ParalNum | R/W | [6 empty] | BatMdlSeria/Paral Num; SPH4-11K used The upper 8 bits indicate the number of series segments； The lower 8 bits indicate the number of parallel sections;
3072 | Reserved
3073 | Reserved
3074 | Reserved
3075 | Reserved
3076 | Reserved
3077 | Reserved
3078 | Reserved
3079 | UpsFunEn |  | Ups function enable or disable | R/W |  |  |  |  | 0 |  | 0:disable 1:enable
3080 | UPSVoltSet |  | UPS output voltage | R/W |  |  |  |  | 0 |  | 0:230V 1:208V 2:240V
3081 | UPSFreqSet |  | UPS output frequency | R/W |  |  |  |  | 0 |  | 0:50Hz 1:60Hz
3082 | bLoadFirstSto pSocSet |  | StopSoc When LoadFirst | R/W |  |  |  |  | 13-100 |  | ratio
3083 | Reserved
3084 | Reserved
3085 | Com Address |  | Communication addr | R/W |  |  |  |  | 1 |  | 1 : Communication addr=1 1 ~ 254 : Communication addr=1~254
3086 | BaudRate |  | Communication BaudRate | R/W |  |  |  |  | 0 |  | 0: 9600 bps 1: 38400 bps
3087 | Serial NO. 1 |  | Serial Number 1-2 | R/W |  |  | ASCII |  |  |  | For battery
3088 | Serial NO. 2 |  | Serial Number 3-4 | R/W |  |  | ASCII
3089 | Serial NO. 3 |  | Serial Number 5-6 | R/W |  |  | ASCII
3090 | Serial NO. 4 |  | Serial Number 7-8 | R/W |  |  | ASCII
3091 | Serial No. 5 |  | Serial Number 9-10 | R/W |  |  | ASCII
3092 | Serial No.6 |  | Serial Number 11-12 | R/W |  |  | ASCII
3093 | Serial No. 7 |  | Serial Number 13-14 | R/W |  |  | ASCII
3094 | Serial No. 8 |  | Serial Number 15-16 | R/W |  |  | ASCII
3095 | BdcResetCmd |  | BDC Reset command | R/W | [6 empty] | 0：Invalid data 1：Reset setting parameters 2：Reset correction parameter 3：Clear historical power
3096 | ARKM3 Code |  | BDCMonitoring software code | R |  |  | ASCII |  |  |  | ZEBA
3097
3098 | DTC |  | DTC | R
3099 | FW Code |  | DSP software code | R |  |  | ASCII
3100
3101 | Processor1 FW Vision |  | DSP Software Version | R |  |  | ASCII
3102 | BusVoltRef |  | Minimum BUS voltage for charging and discharging batteries | R
3103 | ARKM3Ver |  | BDC monitoring software version | R
3104 | BMS_MCUVer sion |  | BMS hardware version information | R | 1
3105 | BMS_FW |  | BMS software version information | R | 1
3106 | BMS_Info |  | BMS ManufacturerName | R | 1
3107 | BMSCommTy pe |  | BMSCommType | R | 1 | [5 empty] | BMSCommunicati on interface type： 0: RS485; 1: CAN;
3108 | Module 4 |  | BDCmodel (4) | R/W | &*11 | [5 empty] | SxxBxx
3109 | Module 3 |  | BDCmodel (3) | R/W | &*11 | [5 empty] | DxxTxx
3110 | Module 2 |  | BDCmodel (2) | R/W | &*11 | [5 empty] | PxxUxx
3111 | Module 1 |  | BDCmodel (1) | R/W | &*11 | [5 empty] | Mxxxx
3112 | Reserved
3113 | unProtocolVe r |  | BDCProtocolVer | R | 1 | [5 empty] | Bit8-bit15 The major version number ranges from 0-256. In principle, it cannot be changed Bit0-bit7 Minor version number [0-256]. If the protocol is changed, you need to update this version No.
3114 | uwCertificatio nVer |  | BDC CertificationVer | R | 1
3115 ~ 3124 | Reserved
US Machine type Time Set
3125 | Time Month1 |  | Use with Time1-9（us） ，Add month time | R/W | [6 empty] | bit0~3:month_L； bit4~7: month_H bit8, 0:disable 1：enable Bit9~15:reserve
3126 | Time Month2 |  | Use with Time10-18（us） ，Add month time | R/W | [6 empty] | With Time Month1
3127 | Time Month3 |  | Use with Time19-27（us） ，Add month time | R/W | [6 empty] | With Time Month1
3128 | Time Month4 |  | Use with Time28-36（us） ，Add month time | R/W | [6 empty] | With Time Month1
3129 | Time 1（us） |  | time1：[starttime~endtime] | R/W | [Charge/ discharg e/counte r | [5 empty] | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst;
[5 empty] | current], [disable/ enable] | [5 empty] | 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0:disable; 1:enable;
3130 |  |  |  | R/W | [6 empty] | bit0~6:min； bit7~11:hour； bit12-13, 0:Weekday 1:Weekend 2:WeeK bit14~15：reserve
3131-3 132 | Time 2（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3133-3 134 | Time 3（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3135-3 136 | Time 4（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3137-3 138 | Time 5（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3139-3 140 | Time 6（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3141-3 142 | Time 7（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3143-3 144 | Time 8（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3145-3 146 | Time9（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3147-3 148 | Time 10（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3149-3 150 | Time 11（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3151-3 152 | Time 12（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3153-3 154 | Time 13（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3155-3 156 | Time 14（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3157-3 158 | Time15（us） |  | Same as above | R/W | [6 empty] | Same as Time 1 （us）
3159-3 160 3161-3 162 3163-3 164 3165-3 166 3167-3 168 3169-3 170 3171-3 172 3173-3 174 3175-3 176 3177-3 178 3179-3 180 3181-3 182 3183-3 184 3185-3 186 3187-3 188 3189-3 190 3191-3 192 3193-3 194 3195-3 196 3197-3 198 3199-3 200 | Time 16（us）Same as above Time 17（us）Same as above Time 18（us）Same as above Time 19（us）Same as above Time 20（us）Same as above Time 21（us）Same as above Time 22（us）Same as above Time 23（us）Same as above Time 24（us）Same as above Time 25（us）Same as above Time 26（us）Same as above Time 27（us）Same as above Time 28（us）Same as above Time 29（us）Same as above Time 30（us）Same as above Time 31（us）Same as above Time 32（us）Same as above Time 33（us）Same as above Time 34（us）Same as above Time 35（us）Same as above Time 36（us）Same as above
3201 | SpecialDay1 |  | SpecialDay1（month，Day） | R/W | [6 empty] | bit0~7:day； bit8~14:month bit15， 0：disable 1： enable
3202 | SpecialDay1_ Time1 |  | Start time | R/W | [6 empty] | bit0~6:min； bit7~11:hour； bit12~14, 0:loadfirst; 1:batfirst； 2:gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable;
3203 |  |  | endtime | R/W | [6 empty] | bit0~6:min； bit7~11:hour； bit12~15：reserve
3204-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
205 | Time2 | [9 empty] | SpecialDay1_Time
1
3206-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
207 | Time3 | [9 empty] | SpecialDay1_Time
1
3208-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
209 | Time4 | [9 empty] | SpecialDay1_Time
1
3210-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
211 | Time5 | [9 empty] | SpecialDay1_Time
1
3212-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
213 | Time6 | [9 empty] | SpecialDay1_Time
1
3214-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
215 | Time7 | [9 empty] | SpecialDay1_Time
1
3216-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
217 | Time8 | [9 empty] | SpecialDay1_Time
1
3218-3 | SpecialDay1_ |  | Same as above | R/W | [6 empty] | Same as
219 | Time9 | [9 empty] | SpecialDay1_Time
1
3220 | SpecialDay2 |  | SpecialDay2（month，Day） | R/W | [6 empty] | bit0~7:day； bit8~14:month bit15， 0：disable 1：enable
3221 | SpecialDay2_ Time1 |  | Start time | R/W | [6 empty] | bit0~6: min； bit7~11: hour； bit12~14, 0: loadfirst; 1: batfirst； 2: gridfirst； 3: anti-reflux bit15, 0: disable; 1: enable;
3222 |  |  | endtime | R/W | [6 empty] | bit0~6: min； bit7~11: hour； bit12~15：reserve
3223-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
224 | Time2 | [9 empty] | SpecialDay2_Time
1
3225-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
226 | Time3 | [9 empty] | SpecialDay2_Time
1
3227-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
228 | Time4 | [9 empty] | SpecialDay2_Time
1
3229-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
230 | Time5 | [9 empty] | SpecialDay2_Time
1
3231-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
232 | Time6 | [9 empty] | SpecialDay2_Time
1
3233-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
234 | Time7 | [9 empty] | SpecialDay2_Time
1
3235-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
236 | Time8 | [9 empty] | SpecialDay2_Time
1
3237-3 | SpecialDay2_ |  | Same as above | R/W | [6 empty] | Same as
238 | Time9 | [9 empty] | SpecialDay2_Time
1
3239-3 249 |  |  | Reserve | R/W
BDC information (support up to 10 parallel BDC)
5000-5039 |  |  | 1
5040-5079 |  |  | 2
5000+(N-1)*40--- 5039+(N-1)*40 |  |  | N

## input registers
4.2 Input Reg
NO. |  | Description | [7 empty] | Value |  |  |  | Unit |  |  | Note
First group
0 | Inverter Status | Inverter run state | [7 empty] | 0:waiting, 1:normal, 3:fault
1 | Ppv H | Input power (high) | [11 empty] | 0.1W
2 | Ppv L | Input power (low) | [11 empty] | 0.1W
3 | Vpv1 | PV1 voltage | [11 empty] | 0.1V
4 | PV1Curr | PV1 input current | [11 empty] | 0.1A
5 | Ppv1 H | PV1 input power(high) | [11 empty] | 0.1W
6 | Ppv1 L | PV1 input power(low) | [11 empty] | 0.1W
7 | Vpv2 | PV2 voltage | [11 empty] | 0.1V
8 | PV2Curr | PV2 input current | [11 empty] | 0.1A
9 | Ppv2 H | PV2 input power (high) | [11 empty] | 0.1W
10 | Ppv2 L | PV2 input power (low) | [11 empty] | 0.1W
11 | Vpv3 | PV3 voltage | [11 empty] | 0.1V
12 | PV3Curr | PV3 input current | [11 empty] | 0.1A
13 | Ppv3 H | PV3 input power (high) | [11 empty] | 0.1W
14 | Ppv3 L | PV3 input power (low) | [11 empty] | 0.1W
15 | Vpv4 | PV4 voltage | [11 empty] | 0.1V
16 | PV4Curr | PV4 input current | [11 empty] | 0.1A
17 | Ppv4 H | PV4 input power (high) | [11 empty] | 0.1W
18 | Ppv4 L | PV4 input power (low) | [11 empty] | 0.1W
19 | Vpv5 | PV5 voltage | [11 empty] | 0.1V
20 | PV5Curr | PV5 input current | [11 empty] | 0.1A
21 | Ppv5H | PV5 input power(high) | [11 empty] | 0.1W
22 | Ppv5 L | PV5 input power(low) | [11 empty] | 0.1W
23 | Vpv6 | PV6 voltage | [11 empty] | 0.1V
24 | PV6Curr | PV6 input current | [11 empty] | 0.1A
25 | Ppv6 H | PV6 input power (high) | [11 empty] | 0.1W
26 | Ppv6 L | PV6 input power (low) | [11 empty] | 0.1W
27 | Vpv7 | PV7 voltage | [11 empty] | 0.1V
28 | PV7Curr | PV7 input current | [11 empty] | 0.1A
29 | Ppv7 H | PV7 input power (high) | [11 empty] | 0.1W
30 | Ppv7 L | PV7 input power (low) | [11 empty] | 0.1W
31 | Vpv8 | PV8 voltage | [11 empty] | 0.1V
32 | PV8Curr | PV8 input current | [11 empty] | 0.1A
33 | Ppv8 H | PV8 input power (high) | [11 empty] | 0.1W
34 | Ppv8 L | PV8 input power (low) | [11 empty] | 0.1W
35 | Pac H | Output power (high) | [11 empty] | 0.1W
36 | Pac L | Output power (low) | [11 empty] | 0.1W
37 | Fac | Grid frequency | [11 empty] | 0.01Hz
38 | Vac1 | Three/single phase grid voltage | [11 empty] | 0.1V
39 | Iac1 | Three/single phase grid output current | [11 empty] | 0.1A
40 | Pac1 H | Three/single phase grid output watt VA (high) | [11 empty] | 0.1VA
41 | Pac1 L | Three/single phase grid output watt VA(low) | [11 empty] | 0.1VA
42 | Vac2 | Three phase grid voltage | [11 empty] | 0.1V
43 | Iac2 | Three phase grid output current | [11 empty] | 0.1A
44 | Pac2 H | Three phase grid output power (high) | [11 empty] | 0.1VA
45 | Pac2 L | Three phase grid output power (low) | [11 empty] | 0.1VA
46 | Vac3 | Three phase grid voltage | [11 empty] | 0.1V
47 | Iac3 | Three phase grid output current | [11 empty] | 0.1A
48 | Pac3 H | Three phase grid output power (high) | [11 empty] | 0.1VA
49 | Pac3 L | Three phase grid output power (low) | [11 empty] | 0.1VA
50 | Vac_RS | Three phase grid voltage | [11 empty] | 0.1V |  |  | Line voltage
51 | Vac_ST | Three phase grid voltage | [11 empty] | 0.1V |  |  | Line voltage
52 | Vac_TR | Three phase grid voltage | [11 empty] | 0.1V |  |  | Line voltage
53 | Eactoday H | Today generate energy (high) | [11 empty] | 0.1kWH
54 | Eac today L | Today generate energy (low) | [11 empty] | 0.1kWH
55 | Eac total H | Total generate energy (high) | [11 empty] | 0.1kWH
56 | Eac total L | Total generate energy (low) | [11 empty] | 0.1kWH
57 | Time total H | Work time total (high) | [11 empty] | 0.5s
58 | Time total L | Work time total (low) | [11 empty] | 0.5s
59 | Epv1_today H | PV1Energy today(high) | [11 empty] | 0.1kWh
60 | Epv1_today L | PV1Energy today (low) | [11 empty] | 0.1kWh
61 | Epv1_total H | PV1Energy total(high) | [11 empty] | 0.1kWh
62 | Epv1_total L | PV1Energy total (low) | [11 empty] | 0.1kWh
63 | Epv2_today H | PV2Energy today(high) | [11 empty] | 0.1kWh
64 | Epv2_today L | PV2Energy today (low) | [11 empty] | 0.1kWh
65 | Epv2_total H | PV2Energy total(high) | [11 empty] | 0.1kWh
66 | Epv2_total L | PV2Energy total (low) | [11 empty] | 0.1kWh
67 | Epv3_today H | PV3 Energy today(high) | [11 empty] | 0.1kWh
68 | Epv3_today L | PV3 Energy today (low) | [11 empty] | 0.1kWh
69 | Epv3_total H | PV3 Energy total(high) | [11 empty] | 0.1kWh
70 | Epv3_total L | PV3 Energy total (low) | [11 empty] | 0.1kWh
71 | Epv4_today H | PV4Energy today(high) | [11 empty] | 0.1kWh
72 | Epv4_today L | PV4Energy today (low) | [11 empty] | 0.1kWh
73 | Epv4_total H | PV4Energy total(high) | [11 empty] | 0.1kWh
74 | Epv4_total L | PV4Energy total (low) | [11 empty] | 0.1kWh
75 | Epv5_today H | PV5Energy today(high) | [11 empty] | 0.1kWh
76 | Epv5_today L | PV5Energy today (low) | [11 empty] | 0.1kWh
77 | Epv5_total H | PV5Energy total(high) | [11 empty] | 0.1kWh
78 | Epv5_total L | PV5Energy total (low) | [11 empty] | 0.1kWh
79 | Epv6_today H | PV6Energy today(high) | [11 empty] | 0.1kWh
80 | Epv6_today L | PV6Energy today (low) | [11 empty] | 0.1kWh
81 | Epv6_total H | PV6Energy total(high) | [11 empty] | 0.1kWh
82 | Epv6_total L | PV6Energy total (low) | [11 empty] | 0.1kWh
83 | Epv7_today H | PV7Energy today(high) | [11 empty] | 0.1kWh
84 | Epv7_today L | PV7Energy today (low) | [11 empty] | 0.1kWh
85 | Epv7_total H | PV7 Energy total(high) | [11 empty] | 0.1kWh
86 | Epv7_total L | PV7Energy total (low) | [11 empty] | 0.1kWh
87 | Epv8_today H | PV8Energy today(high) | [11 empty] | 0.1kWh
88 | Epv8_today L | PV8Energy today (low) | [11 empty] | 0.1kWh
89 | Epv8_total H | PV8Energy total(high) | [11 empty] | 0.1kWh
90 | Epv8_total L | PV8Energy total (low) | [11 empty] | 0.1kWh
91 | Epv_total H | PV Energy total(high) | [11 empty] | 0.1kWh
92 | Epv_total L | PV Energy total (low) | [11 empty] | 0.1kWh
93 | Temp1 | Inverter temperature | [11 empty] | 0.1C
94 | Temp2 | The inside IPM in inverter Temperature | [11 empty] | 0.1C
95 | Temp3 | Boost temperature | [11 empty] | 0.1C
96 | Temp4 | [15 empty] | reserved
97 | uwBatVolt_DSP | BatVolt_DSP | [11 empty] | 0.1V |  |  | BatVolt(DSP)
98 | P Bus Voltage | P Bus inside Voltage | [11 empty] | 0.1V
99 | N Bus Voltage | N Bus inside Voltage | [11 empty] | 0.1V
100 | IPF | Inverter output PF now | [7 empty] | 0-20000
101 | RealOPPercent | Real Output power Percent | [11 empty] | 1%
102 | OPFullwatt H | Output Maxpower Limited high
103 | OPFullwatt L | Output Maxpower Limited low | [11 empty] | 0.1W
104 | DeratingMode | DeratingMode | [7 empty] | 0:no derate; 1:PV; 2:*; 3:Vac; 4:Fac; 5:Tboost; 6:Tinv; 7:Control; 8:*; 9:*OverBack ByTime;
105 | Fault Maincode | Inverter fault maincode
106
107 | Fault Subcode | Inverter fault subcode
108 | RemoteCtrlEn | / | [7 empty] | 0.Load First 1.BatFirst 2.Grid |  |  |  | / |  |  | StoragePow er (SPA)
109 | RemoteCtrlPow er | / | [11 empty] | / |  |  | StoragePow er (SPA)
110 | Warning bit H | Warning bit H
111 | Warn Subcode | Inverter warn subcode
112 | Warn Maincode | Inverter warn maincode
| EACharge_Today _H | ACCharge energy today | [11 empty] | 0.1kwh |  |  | Storage Power
113 | real Power Percent | real Power Percent | [7 empty] | 0-100 |  |  |  | % |  |  | MAX
| EACharge_Today _L | ACCharge energy today | [11 empty] | 0.1kwh |  |  | Storage Power
114 | inv start delay time | inv start delay time | [14 empty] | MAX
| EACharge_Total _H | ACCharge energy total | [11 empty] | 0.1kwh |  |  | Storage Power
115 | bINVAllFaultCod e | bINVAllFaultCode | [14 empty] | MAX
| EACharge_Total _L | ACCharge energy total | [11 empty] | 0.1kwh |  |  | Storage Power
116 | AC charge Power_H | Grid power to local load | [11 empty] | 0.1kwh |  |  | Storage Power
117 | AC charge Power_L | Grid power to local load | [11 empty] | 0.1kwh |  |  | Storage Power
118 | Priority | 0:Load First | [14 empty] | Storage
|  | 1:Battery First 2:Grid First | [14 empty] | Power
119 | Battery Type | 0：Lead-acid 1：Lithium battery | [14 empty] | Storage Power
120 | AutoProofreadC MD | Aging mode Auto-calibration command | [14 empty] | Storage Power
… | reserved | [15 empty] | reserved
124 | reserved | [15 empty] | reserved
Second group
125 | PID PV1+ Voltage |  | PID PV1PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
126 | PID PV1+ Current |  | PID PV1PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
127 | PID PV2+ Voltage |  | PID PV2PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
128 | PID PV2+ Current |  | PID PV2PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
129 | PID PV3+ Voltage |  | PID PV3PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
130 | PID PV3+ Current |  | PID PV3PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
131 | PID PV4+ Voltage |  | PID PV4PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
132 | PID PV4+ Current |  | PID PV4PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
133 | PID PV5+ Voltage |  | PID PV5PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
134 | PID PV5+ Current |  | PID PV5PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
135 | PID PV6+ Voltage |  | PID PV6PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
136 | PID PV6+ Current |  | PID PV6PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
137 | PID PV7+ Voltage |  | PID PV7PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
138 | PID PV7+ Current |  | PID PV7PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
139 | PID PV8+ Voltage |  | PID PV8PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
140 | PID PV8+ Current |  | PID PV8PE Curr | [6 empty] | -10~10mA |  |  |  | 0.1mA
141 | PID Status |  | Bit0~7:PID Working Status 1:Wait Status 2:Normal Status 3:Fault Status Bit8~15:Reversed | [6 empty] | 0~3
142 | V _String1 |  | PV String1 voltage | [10 empty] | 0.1V
143 | Curr _String1 |  | PV String1 current | [6 empty] | -15~15A |  |  |  | 0.1A
144 | V _String2 |  | PV String2 voltage | [10 empty] | 0.1V
145 | Curr _String2 |  | PV String2 current | [6 empty] | -15~15A |  |  |  | 0.1A
146 | V _String3 |  | PV String3 voltage | [10 empty] | 0.1V
147 | Curr _String3 |  | PV String3 current | [6 empty] | -15~15A |  |  |  | 0.1A
148 | V _String4 |  | PV String4 voltage | [10 empty] | 0.1V
149 | Curr _String4 |  | PV String4 current | [6 empty] | -15~15A |  |  |  | 0.1A
150 | V _String5 |  | PV String5 voltage | [10 empty] | 0.1V
151 | Curr _String5 |  | PV String5 current | [6 empty] | -15~15A |  |  |  | 0.1A
152 | V _String6 |  | PV String6 voltage | [10 empty] | 0.1V
153 | Curr _String6 |  | PV String6 current | [6 empty] | -15~15A |  |  |  | 0.1A
154 | V _String7 |  | PV String7 voltage | [10 empty] | 0.1V
155 | Curr _String7 |  | PV String7 current | [6 empty] | -15~15A |  |  |  | 0.1A
156 | V _String8 |  | PV String8 voltage | [10 empty] | 0.1V
157 | Curr _String8 |  | PV String8 current | [6 empty] | -15A~15A |  |  |  | 0.1A
158 | V _String9 |  | PV String9 voltage | [10 empty] | 0.1V
159 | Curr _String9 |  | PV String9 current | [6 empty] | -15A~15A |  |  |  | 0.1A
160 | V _String10 |  | PV String10 voltage | [10 empty] | 0.1V
161 | Curr _String10 |  | PV String10 current | [6 empty] | -15~15A |  |  |  | 0.1A
162 | V _String11 |  | PV String11 voltage | [10 empty] | 0.1V
163 | Curr _String11 |  | PV String11 current | [6 empty] | -15~15A |  |  |  | 0.1A
164 | V _String12 |  | PV String12 voltage | [10 empty] | 0.1V
165 | Curr _String12 |  | PV String12 current | [6 empty] | -15~15A |  |  |  | 0.1A
166 | V _String13 |  | PV String13 voltage | [10 empty] | 0.1V
167 | Curr _String13 |  | PV String13 current | [6 empty] | -15A~15A |  |  |  | 0.1A
168 | V _String14 |  | PV String14 voltage | [10 empty] | 0.1V
169 | Curr _String14 |  | PV String14 current | [6 empty] | -15~15A |  |  |  | 0.1A
170 | V _String15 |  | PV String15 voltage | [10 empty] | 0.1V
171 | Curr _String15 |  | PV String15 current | [6 empty] | -15~15A |  |  |  | 0.1A
172 | V _String16 |  | PV String16 voltage | [10 empty] | 0.1V
173 | Curr _String16 |  | PV String16 current | [6 empty] | -15~15A |  |  |  | 0.1A
174 | StrUnmatch |  | Bit0~15: String1~16 unmatch | [13 empty] | suggestive
175 | StrCurrentUnblan ce |  | Bit0~15: String1~16 current unblance | [13 empty] | suggestive
176 | StrDisconnect |  | Bit0~15: String1~16 disconnect | [13 empty] | suggestive
177 | PIDFaultCode |  | Bit0:Output over voltage Bit1: ISO fault Bit2: BUS voltage abnormal Bit3~15:reserved
178 | String Prompt |  | String Prompt Bit0:String Unmatch Bit1:StrDisconnect Bit2:StrCurrentUnblance
Bit3~15:reserved
179 | PV Warning Value |  | PV Warning Value
180 | DSP075 Warning Value |  | DSP075 Warning Value
181 | DSP075 Fault Value |  | DSP075 Fault Value
182 | DSP067 Debug Data1 |  | DSP067 Debug Data1
183 | DSP067 Debug Data2 |  | DSP067 Debug Data2
184 | DSP067 Debug Data3 |  | DSP067 Debug Data3
185 | DSP067 Debug Data4 |  | DSP067 Debug Data4
186 | DSP067 Debug Data5 |  | DSP067 Debug Data5
187 | DSP067 Debug Data6 |  | DSP067 Debug Data6
188 | DSP067 Debug Data7 |  | DSP067 Debug Data7
189 | DSP067 Debug Data8 |  | DSP067 Debug Data8
190 | DSP075 Debug Data1 |  | DSP075 Debug Data1
191 | DSP075 Debug Data2 |  | DSP075 Debug Data2
192 | DSP075 Debug Data3 |  | DSP075 Debug Data3
193 | DSP075 Debug Data4 |  | DSP075 Debug Data4
194 | DSP075 Debug Data55 |  | DSP075 Debug Data5
195 | DSP075 Debug Data6 |  | DSP075 Debug Data6
196 | DSP075 Debug Data7 |  | DSP075 Debug Data7
197 | DSP075 Debug Data8 |  | DSP075 Debug Data8
198 | bUSBAgingTestOk Flag |  | USBAgingTestOkFlag | [6 empty] | 0-1
199 | bFlashEraseAging OkFlag |  | FlashEraseAgingOkFlag | [6 empty] | 0-1
200 | PVISO |  | PVISOValue | [10 empty] | KΩ
201 | R_DCI |  | R DCI Curr | [10 empty] | 0.1mA
202 | S_DCI |  | S DCI Curr | [10 empty] | 0.1mA
203 | T_DCI |  | T DCI Curr | [10 empty] | 0.1mA
204 | PID_Bus |  | PIDBusVolt | [10 empty] | 0.1V
205 | GFCI |  | GFCI Curr | [10 empty] | mA
206 | SVG/APF Status+SVGAPFEq ualRatio |  | SVG/APF Status+SVGAPFEqualRatio | [6 empty] | High 8 bit： SVGAPFEqua lRatio Low 8 bit： SVG/APF Status 0:None 1:SVG Run 2:APF Run 3:SVG/APF Run
207 | CT_I _R |  | R phase load side current for SVG | [10 empty] | 0.1A
208 | CT_I _S |  | S phase load side current for SVG | [10 empty] | 0.1A
209 | CT_I _T |  | T phase load side current for SVG | [10 empty] | 0.1A
210 | CT_Q _R H |  | R phase load side output reactive power for SVG(High) | [10 empty] | 0.1Var
211 | CT_Q _R L |  | R phase load side output reactive power for SVG(low) | [10 empty] | 0.1Var
212 | CT_Q _S H |  | S phase load side output reactive power for SVG(High) | [10 empty] | 0.1Var
213 | CT_Q _S L |  | S phase load side output reactive power for SVG(low) | [10 empty] | 0.1Var
214 | CT_Q _T H |  | T phase load side output reactive power for SVG(High) | [10 empty] | 0.1Var
215 | CT_Q _T L |  | T phase load side output reactive power for SVG(low) | [10 empty] | 0.1Var
216 | CT HAR_I_R |  | R phase load side harmonic | [10 empty] | 0.1A
217 | CT HAR_I_S |  | S phase load side harmonic | [10 empty] | 0.1A
218 | CT HAR_I_T |  | T phase load side harmonic | [10 empty] | 0.1A
219 | COMP_Q _R H |  | R phase compensate reactive power for SVG(High) | [10 empty] | 0.1Var
220 | COMP_Q _R L |  | R phase compensate reactive power for SVG(low) | [10 empty] | 0.1Var
221 | COMP_Q _S H |  | S phase compensate reactive power for SVG(High) | [10 empty] | 0.1Var
222 | COMP_Q _S L |  | S phase compensate reactive power | [10 empty] | 0.1Var
for SVG(low)
223 | COMP_Q _T H |  | T phase compensate reactive power for SVG(High) | [10 empty] | 0.1Var
224 | COMP_Q _T L |  | T phase compensate reactive power for SVG(low) | [10 empty] | 0.1Var
225 | COMP HAR_I_R |  | R phase compensate harmonic for SVG | [10 empty] | 0.1A
226 | COMP HAR_I_S |  | S phase compensate harmonic for SVG | [10 empty] | 0.1A
227 | COMP HAR_I_T |  | T phase compensate harmonic for SVG | [10 empty] | 0.1A
228 | bRS232AgingTest OkFlag |  | RS232AgingTestOkFlag | [6 empty] | 0-1
229 | bFanFaultBit |  | Bit0: Fan 1 fault bit Bit1: Fan 2 fault bit Bit2: Fan 3 fault bit Bit3: Fan 4 fault bit Bit4-7: Reserved
230 | Sac H |  | Output apparent power H | [10 empty] | 0.1W
231 | Sac L |  | Output apparent power L | [10 empty] | 0.1W
232 | ReActPowerH |  | Real Output Reactive Power H | [6 empty] | Int32 |  |  |  | 0.1W
233 | ReActPowerL |  | Real Output Reactive Power L
234 | ReActPowerMaxH |  | Nominal Output Reactive Power H | [10 empty] | 0.1var
235 | ReActPowerMaxL |  | Nominal Output Reactive Power L
236 | ReActPower_Total H |  | Reactive power generation | [10 empty] | 0.1kwh
237 | ReActPower_Total L |  | Reactive power generation
238 | bAfciStatus |  | 0：Waiting 1：Self-check state 2：Detect pull arc state 3：Fault 4：Update
239 | uwPresentFFTValu e [CHANNEL_A] |  | PresentFFTValue [CHANNEL_A]
240 | uwPresentFFTValu e [CHANNEL_B] |  | PresentFFTValue [CHANNEL_B]
241 | DSP067 Debug Data1 |  | DSP067 Debug Data1
242 | DSP067 Debug Data2 |  | DSP067 Debug Data2
243 | DSP067 Debug |  | DSP067 Debug Data3
Data3
244 | DSP067 Debug Data4 |  | DSP067 Debug Data4
245 | DSP067 Debug Data5 |  | DSP067 Debug Data5
246 | DSP067 Debug Data6 |  | DSP067 Debug Data6
247 | DSP067 Debug Data7 |  | DSP067 Debug Data7
248 | DSP067 Debug Data8 |  | DSP067 Debug Data8
249 | [16 empty] | reserved
The eighth group for PV9-PV16 information
875 | Vpv9 |  | PV9 voltage | [10 empty] | 0.1V
876 | PV9Curr |  | PV9 Input current | [10 empty] | 0.1A
877 | Ppv9 H |  | PV9 input power (High) | [10 empty] | 0.1W
878 | Ppv9 L |  | PV9 input power (Low) | [10 empty] | 0.1W
879 | Vpv10 |  | PV10 voltage | [10 empty] | 0.1V
880 | PV10Curr |  | PV10 Input current | [10 empty] | 0.1A
881 | Ppv10 H |  | PV10 input power (High) | [10 empty] | 0.1W
882 | Ppv10 L |  | PV10 input power (Low) | [10 empty] | 0.1W
883 | Vpv11 |  | PV11 voltage | [10 empty] | 0.1V
884 | PV11Curr |  | PV11 Input current | [10 empty] | 0.1A
885 | Ppv11 H |  | PV11 input power (High) | [10 empty] | 0.1W
886 | Ppv11 L |  | PV11 input power (Low) | [10 empty] | 0.1W
887 | Vpv12 |  | PV12 voltage | [10 empty] | 0.1V
888 | PV12Curr |  | PV12 Input current | [10 empty] | 0.1A
889 | Ppv12 H |  | PV12 input power (High) | [10 empty] | 0.1W
890 | Ppv12 L |  | PV12 input power (Low) | [10 empty] | 0.1W
891 | Vpv13 |  | PV13 voltage | [10 empty] | 0.1V
892 | PV13Curr |  | PV13 Input current | [10 empty] | 0.1A
893 | Ppv13H |  | PV13 input power (High) | [10 empty] | 0.1W
894 | Ppv13 L |  | PV13 input power (Low) | [10 empty] | 0.1W
895 | Vpv14 |  | PV14 voltage | [10 empty] | 0.1V
896 | PV14Curr |  | PV14 Input current | [10 empty] | 0.1A
897 | Ppv14 H |  | PV14 input power (High) | [10 empty] | 0.1W
898 | Ppv14 L |  | PV14 input power (Low) | [10 empty] | 0.1W
899 | Vpv15 |  | PV15 voltage | [10 empty] | 0.1V
900 | PV15Curr |  | PV15 Input current | [10 empty] | 0.1A
901 | Ppv15 H |  | PV15 input power (High) | [10 empty] | 0.1W
902 | Ppv15 L |  | PV15 input power (Low) | [10 empty] | 0.1W
903 | Vpv16 |  | PV16 voltage | [10 empty] | 0.1V
904 | PV16Curr |  | PV16 Input current | [10 empty] | 0.1A
905 | Ppv16 H |  | PV16 input power (High) | [10 empty] | 0.1W
906 | Ppv16 L |  | PV16 input power (Low) | [10 empty] | 0.1W
907 | Epv9_today H |  | PV9 energy today (High) | [10 empty] | 0.1kWh
908 | Epv9_today L |  | PV9 energy today (Low) | [10 empty] | 0.1kWh
909 | Epv9_total H |  | PV9 energy total (High) | [10 empty] | 0.1kWh
910 | Epv9_total L |  | PV9 energy total (Low) | [10 empty] | 0.1kWh
911 | Epv10_today H |  | PV10 energy today (High) | [10 empty] | 0.1kWh
912 | Epv10_today L |  | PV10 energy today (Low) | [10 empty] | 0.1kWh
913 | Epv10_total H |  | PV10 energy total (High) | [10 empty] | 0.1kWh
914 | Epv10_total L |  | PV10 energy total (Low) | [10 empty] | 0.1kWh
915 | Epv11_today H |  | PV11 energy today (High) | [10 empty] | 0.1kWh
916 | Epv11_today L |  | PV11 energy today (Low) | [10 empty] | 0.1kWh
917 | Epv11_total H |  | PV11 energy total (High) | [10 empty] | 0.1kWh
918 | Epv11_total L |  | PV11 energy total (Low) | [10 empty] | 0.1kWh
919 | Epv12_today H |  | PV12 energy today (High) | [10 empty] | 0.1kWh
920 | Epv12_today L |  | PV12 energy today (Low) | [10 empty] | 0.1kWh
921 | Epv12_total H |  | PV12 energy total (High) | [10 empty] | 0.1kWh
922 | Epv12_total L |  | PV12 energy total (Low) | [10 empty] | 0.1kWh
923 | Epv13_today H |  | PV13 energy today (High) | [10 empty] | 0.1kWh
924 | Epv13_today L |  | PV13 energy today (Low) | [10 empty] | 0.1kWh
925 | Epv13_total H |  | PV13 energy total (High) | [10 empty] | 0.1kWh
926 | Epv13_total L |  | PV13 energy total (Low) | [10 empty] | 0.1kWh
927 | Epv14_today H |  | PV14 energy today (High) | [10 empty] | 0.1kWh
928 | Epv14_today L |  | PV14 energy today (Low) | [10 empty] | 0.1kWh
929 | Epv14_total H |  | PV14 energy total (High) | [10 empty] | 0.1kWh
930 | Epv14_total L |  | PV14 energy total (Low) | [10 empty] | 0.1kWh
931 | Epv15_today H |  | PV15 energy today (High) | [10 empty] | 0.1kWh
932 | Epv15_today L |  | PV15 energy today (Low) | [10 empty] | 0.1kWh
933 | Epv15_total H |  | PV15 energy total (High) | [10 empty] | 0.1kWh
934 | Epv15_total L |  | PV15 energy total (Low) | [10 empty] | 0.1kWh
935 | Epv16_today H |  | PV16 energy today (High) | [10 empty] | 0.1kWh
936 | Epv16_today L |  | PV16 energy today (Low) | [10 empty] | 0.1kWh
937 | Epv16_total H |  | PV16 energy total (High) | [10 empty] | 0.1kWh
938 | Epv16_total L |  | PV16 energy total (Low) | [10 empty] | 0.1kWh
939 | PID PV9+ Voltage |  | PID PV9PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
940 | PID PV9+ Current |  | PID PV9PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
941 | PID PV10+ Voltage |  | PID PV10PE/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
942 | PID PV10+ Current |  | PID PV10PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
943 | PID PV11+ Voltage |  | PID PV11PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
944 | PID PV11+ Current |  | PID PV11PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
945 | PID PV12+ Voltage |  | PID PV12PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
946 | PID PV12+ Current |  | PID PV12PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
947 | PID PV13+ Voltage |  | PID PV13PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
948 | PID PV13+ Current |  | PID PV13PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
949 | PID PV14+ Voltage |  | PID PV14PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
950 | PID PV14+ Current |  | PID PV14PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
951 | PID PV15+ Voltage |  | PID PV15PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
952 | PID PV15+ Current |  | PID PV15PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
953 | PID PV16+ Voltage |  | PID PV16PE Volt/ Flyspan voltage (MAX HV) | [6 empty] | 0~1000V |  |  |  | 0.1V
954 | PID PV16+ Current |  | PID PV16PE Current | [6 empty] | -10~10mA |  |  |  | 0.1mA
955 | V _String17 |  | PV String 17 voltage | [10 empty] | 0.1V
956 | Curr _String17 |  | PV String 17 Current | [6 empty] | -15~15A |  |  |  | 0.1A
957 | V _String18 |  | PV String 18 voltage | [10 empty] | 0.1V
958 | Curr _String18 |  | PV String 18 Current | [6 empty] | -15~15A |  |  |  | 0.1A
959 | V _String19 |  | PV String 19 voltage | [10 empty] | 0.1V
960 | Curr _String19 |  | PV String 19 Current | [6 empty] | -15~15A |  |  |  | 0.1A
961 | V _String20 |  | PV String 20 voltage | [10 empty] | 0.1V
962 | Curr _String20 |  | PV String 20 Current | [6 empty] | -15~15A |  |  |  | 0.1A
963 | V _String21 |  | PV String 21 voltage | [10 empty] | 0.1V
964 | Curr _String21 |  | PV String 21 Current | [6 empty] | -15~15A |  |  |  | 0.1A
965 | V _String22 |  | PV String22 voltage | [10 empty] | 0.1V
966 | Curr _String22 |  | PV String 22 Current | [6 empty] | -15~15A |  |  |  | 0.1A
967 | V _String23 |  | PV String 23 voltage | [10 empty] | 0.1V
968 | Curr _String23 |  | PV String 23 Current | [6 empty] | -15~15A |  |  |  | 0.1A
969 | V _String24 |  | PV String 24 voltage | [10 empty] | 0.1V
970 | Curr _String24 |  | PV String 24 Current | [6 empty] | -15A~15A |  |  |  | 0.1A
971 | V _String25 |  | PV String 25 voltage | [10 empty] | 0.1V
972 | Curr _String25 |  | PV String 25 Current | [6 empty] | -15A~15A |  |  |  | 0.1A
973 | V _String26 |  | PV String 26 voltage | [10 empty] | 0.1V
974 | Curr _String26 |  | PV String 26 Current | [6 empty] | -15~15A |  |  |  | 0.1A
975 | V _String27 |  | PV String 27 voltage | [10 empty] | 0.1V
976 | Curr _String27 |  | PV String 27 Current | [6 empty] | -15~15A |  |  |  | 0.1A
977 | V _String28 |  | PV String 28 voltage | [10 empty] | 0.1V
978 | Curr _String28 |  | PV String 28 Current | [6 empty] | -15~15A |  |  |  | 0.1A
979 | V _String29 |  | PV String 29 voltage | [10 empty] | 0.1V
980 | Curr _String29 |  | PV String 29 Current | [6 empty] | -15A~15A |  |  |  | 0.1A
981 | V _String30 |  | PV String 30 voltage | [10 empty] | 0.1V
982 | Curr _String30 |  | PV String 30 Current | [6 empty] | -15~15A |  |  |  | 0.1A
983 | V _String31 |  | PV String 31 voltage | [10 empty] | 0.1V
984 | Curr _String31 |  | PV String 31 Current | [6 empty] | -15~15A |  |  |  | 0.1A
985 | V _String32 |  | PV String 32 voltage | [10 empty] | 0.1V
986 | Curr _String32 |  | PV String 32 Current | [6 empty] | -15~15A |  |  |  | 0.1A
987 | StrUnmatch2 |  | Bit0~15: String 17~32 unmatch
988 | StrCurrentUnblan ce2 |  | Bit0~15:String 17~32 current unblance
989 | StrDisconnect2 |  | Bit0~15: String 17~32 disconnect
990 | PV Warning Value |  | PV Warning Value (PV9-PV16) Contains PV9~16 abnormal ， 和 Boost9~16 Drive anomalies
991 | StrWaringvalue1 |  | string1~string16 abnormal
992 | StrWaringvalue2 |  | string17~string32 abnormal
……
999 | SystemCmd |  | M3 to DSP system command | [13 empty] | system command
Ninth group for Storage power
1000 | uwSysWorkMode |  |  | System work mode |  |  |  |  | 0x00:waiting module 0x01: Self-test mode, optional 0x02 : Reserved 0x03：SysFault module 0x04: Flash module | [5 empty] | Theworkingmode displayed by the monitoring to the customer is： 0x00: waiting module 0x01: Self-test mode, 0x03:fault module 0x04:flash
[9 empty] | 0x05 ： PVBATOnline module, 0x06 ： BatOnline module, 0x07 ： PVOfflineMod e module, 0x08 ： BatOfflineMo de module, | [5 empty] | module 0x05¦0x06¦0x07¦0 x08:normal module
1001 | Systemfault word0 |  |  | System fault word0 | [10 empty] | Please refer thefault description Hybrid |  |  |  |  | to of
1002 | Systemfault word1 |  |  | System fault word1
1003 | Systemfault word2 |  |  | System fault word2
1004 | Systemfault word3 |  |  | System fault word3
1005 | Systemfault word4 |  |  | System fault word4
1006 | Systemfault word5 |  |  | System fault word5
1007 | Systemfault word6 |  |  | System fault word6
1008 | Systemfault word7 |  |  | System fault word7
1009 | Pdischarge1 H |  |  | Discharge power(high) | [8 empty] | 0.1W
1010 | Pdischarge1 L |  |  | Discharge power (low) | [8 empty] | 0.1W
1011 | Pcharge1 H |  |  | Charge power(high) | [8 empty] | 0.1W
1012 | Pcharge1 L |  |  | Charge power (low) | [8 empty] | 0.1W
1013 | Vbat |  |  | Battery voltage | [8 empty] | 0.1V
1014 | SOC |  |  | State of charge Capacity |  |  |  |  | 0-100 |  |  |  | 1% |  | lith/leadacid
1015 | Pactouser R |  |  | AC power to user H | [8 empty] | 0.1w
1016 | Pactouser R |  |  | AC power to user L | [8 empty] | 0.1w
1017 | Pactouser S |  |  | Pactouser S |  | H | [6 empty] | 0.1w
1018 | Pactouser S |  |  | Pactouser S |  | L | [6 empty] | 0.1w
1019 | Pactouser T |  |  | Pactouser T |  | H | [6 empty] | 0.1w
1020 | Pactouser T |  |  | Pactouser T |  | H | [6 empty] | 0.1w
1021 | PactouserTotal H |  |  | AC power to user total H | [8 empty] | 0.1w
1022 | PactouserTotal L |  |  | AC power to user total L | [8 empty] | 0.1w
1023 | Pac to grid R |  |  | AC power to grid H | [8 empty] | 0.1w |  | Ac output
1024 | Pac to grid R |  |  | AC power to grid L | [8 empty] | 0.1w
1025 | Pactogrid S | [11 empty] | 0.1w
1026 | Pactogrid S | [11 empty] | 0.1w
1027 | Pactogrid T H | [10 empty] | 0.1w
1028 | Pactogrid T L | [10 empty] | 0.1w
1029 | Pactogrid total H |  |  | AC power to grid total H | [7 empty] | 0.1w
1030 | Pactogrid total L |  |  | AC power to grid total L | [7 empty] | 0.1w
1031 | PLocalLoad R H |  |  | INV power to local load H | [7 empty] | 0.1w
1032 | PLocalLoad R L |  |  | INV power to local load L | [7 empty] | 0.1w
1033 | PLocalLoad S H | [10 empty] | 0.1w
1034 | PLocalLoad S L | [10 empty] | 0.1w
1035 | PLocalLoadT H | [10 empty] | 0.1w
1036 | PLocalLoadT L | [10 empty] | 0.1w
1037 | PLocalLoad total H |  |  | INV power to local load total H | [7 empty] | 0.1w
1038 | PLocalLoad total L |  |  | INV power to local load total L | [7 empty] | 0.1w
1039 | IPM Temperature |  |  | REC Temperature | [7 empty] | 0.1℃ |  |  | No use
1040 | Battery Temperature |  |  | Battery Temperature | [7 empty] | 0.1℃ |  |  | Lead acid/lithium battery temp
1041 | SP DSP Status |  |  | SP state | [10 empty] | CHG/DisCHG
1042 | SP Bus Volt |  |  | SP BUS2 Volt | [7 empty] | 0.1V
1043
Power generation data
1044 |  | Energy to user today high | [9 empty] | 0.1kWh
1045 |  | Energy to user today low | [9 empty] | 0.1kWh
1046 |  | Energy to user total high | [9 empty] | 0.1kWh
1047 |  | Energy to user total high | [9 empty] | 0.1kWh
1048 |  | Energy to grid today high | [9 empty] | 0.1kWh
1049 |  | Energy to grid today low | [9 empty] | 0.1kWh
1050 |  | Energy to grid total high | [9 empty] | 0.1kWh
1051 |  | Energy to grid total high | [9 empty] | 0.1kWh
1052 |  | Discharge energy1 today | [9 empty] | 0.1kWh
1053 |  | Discharge energy1 today | [9 empty] | 0.1kWh
1054 |  | Total discharge energy1 (high) | [9 empty] | 0.1kWh
1055 |  | Total discharge energy1 (low) | [9 empty] | 0.1kWh
1056 |  | Charge1 energy today | [9 empty] | 0.1kWh
1057 |  | Charge1 energy today | [9 empty] | 0.1kWh
1058 |  | Charge1 energy total | [9 empty] | 0.1kWh
1059 |  | Charge1 energy total | [9 empty] | 0.1kWh
1060 |  | Local load energy today | [9 empty] | 0.1kWh
1061 |  | Local load energy today | [9 empty] | 0.1kWh
1062 |  | Local load energy total | [9 empty] | 0.1kWh
1063 |  | Local load energy total | [9 empty] | 0.1kWh
1064 |  | ExportLimitApparentPower H | [9 empty] | 0.1kWh |  |  | ApparentPower
1065 |  | ExportLimitApparentPower L | [9 empty] | 0.1kWh |  |  | ApparentPower
1066 |  | / | [6 empty] | / |  |  | / |  |  | reserved
1067 |  | UPSfrequency | [6 empty] | 5000/6000 |  |  | 0.01Hz
1068 |  | UPS phase R output voltage | [6 empty] | 2300 |  |  | 0.1V
1069 |  | UPS phase R output current | [9 empty] | 0.1A
1070 |  | UPS phase R output power (H) | [9 empty] | 0.1VA
1071 |  | UPS phase R output power (L) | [9 empty] | 0.1VA
1072 |  | UPS phase S output voltage | [9 empty] | 0.1V
1073 |  | UPS phase S output current | [9 empty] | 0.1A |  |  | No use
1074 |  | UPS phase S output power (H) | [9 empty] | 0.1VA
1075 |  | UPS phase S output power (L) | [9 empty] | 0.1VA
1076 |  | UPS phase T output voltage | [9 empty] | 0.1V
1077 |  | UPS phase T output current | [9 empty] | 0.1A |  |  | No use
1078 |  | UPS phase T output power (H) | [9 empty] | 0.1VA
1079 |  | UPS phase T output power (L) | [9 empty] | 0.1VA
1080 |  | Load percent of UPS ouput | [6 empty] | 0-100 |  |  | 1%
1081 |  | Power factor | [6 empty] | 0-2 |  |  | 0.1 |  |  | Primary Value+1
1082 | BMS_StatusOld | StatusOld from BMS | [6 empty] | Detail information, refer to document:GrowattxxSxx P ESS Protocol;
1083 | BMS_Status | Status from BMS | [12 empty] | W/R
1084 | BMS_ErrorOld | Error info Old from BMS
1085 | BMS_Error | Errorinfomation from BMS
1086 | BMS_SOC | SOC from BMS | [12 empty] | R SPH6K
1087 | BMS_BatteryVol t | Battery voltage from BMS | [12 empty] | R SPH6K
1088 | BMS_BatteryCur r | Battery current from BMS
1089 | BMS_BatteryTe mp | Battery temperature from BMS
1090 | BMS_MaxCurr | Max. charge/discharge current from BMS (pylon)
1091 | BMS_GaugeRM | Gauge RM from BMS
1092 | BMS_GaugeFCC | Gauge FCC from BMS
1093 | BMS_FW
1094 | BMS_DeltaVolt | Delta V from BMS
1095 | BMS_CycleCnt | Cycle Count from BMS
1096 | BMS_SOH | SOH from BMS
1097 | BMS_ConstantV olt | CV voltage from BMS
1098 | BMS_WarnInfoO ld | Warning info old from BMS
1099 | BMS_WarnInfo | Warning info from BMS
1100 | BMS_GaugeICCu rr | Gauge IC current from BMS
1101 | BMS_MCUVersi on | MCU Software version from BMS
1102 | BMS_GaugeVers ion | Gauge Version from BMS
1103 | BMS_wGaugeFR Version_ L | Gauge FR Version L16 from BMS
1104 | BMS_wGaugeFR Version_H | Gauge FR Version H16 from BMS
1105 | BMS_BMSInfo | BMSInformation from BMS
1106 | BMS_PackInfo | Pack Information from BMS
1107 | BMS_UsingCap | Using Cap from BMS
1108 | uwMaxCellVolt | Maximum single battery voltage | [8 empty] | 0.001V
1109 | uwMinCellVolt | Lowest single battery voltage | [8 empty] | 0.001V
1110 | bModuleNum | Battery parallel number | [8 empty] | 1
1111 |  | Number of batteries | [8 empty] | 1
1112 | uwMaxVoltCellN o | MaxVoltCellNo | [8 empty] | 1
1113 | uwMinVoltCellN o | MinVoltCellNo | [8 empty] | 1
1114 | uwMaxTemprCe ll_10T | MaxTemprCell_10T | [8 empty] | 0.1℃
1115 | uwMinTemprCel l_10T | MinTemprCell_10T | [8 empty] | 0.1℃
1116 | uwMaxTemprCe llNo | MaxVoltTemprCellNo | [8 empty] | 1
1117 | uwMinTemprCel | MinVoltTemprCellNo | [8 empty] | 1
lNo
1118 | Protect pack ID | Faulty Battery Address | [8 empty] | 1
1119 | MaxSOC | Parallel maximum SOC | [8 empty] | 1%
1120 | MinSOC | Parallel minimum SOC | [8 empty] | 1%
1121 | BMS_Error2 | Battery Protection 2 | [8 empty] | - |  |  |  | CAN ID ： 0x323 Byte4~5
1122 | BMS_Error3 | Battery Protection3 | [8 empty] | - |  |  |  | CAN ID ： 0x323 Byte6
1123 | BMS_WarnInfo2 | Battery Warn2 | [8 empty] | - |  |  |  | CAN ID ： 0x323 Byte7
1124 | AC Charge Energy Today H | AC Charge Energy today | [6 empty] | kwh | [5 empty] | Energy today
Ninth group reserved for storage power
1125 | ACCharge Energy TodayL | AC Charge Energy today | [6 empty] | kwh
1126 | AC Charge Energy Total H | [13 empty] | Energy total
1127 | ACCharge Energy Total L
1128 | AC Power | AC Charge Power | [6 empty] | W
1129 | AC Power L | AC Charge Power | [6 empty] | w
1130 | 70% INV Power adjust | uwGridPower_70_AdjEE_SP | [6 empty] | W
1131 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | [6 empty] | For SPA connect inverter | [5 empty] | SPA used
1132 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low | [12 empty] | SPA used
1133 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | [6 empty] | R |  |  | 0.1kWh |  |  | SPA |  |  | used
1134 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | [6 empty] | R |  |  | 0.1kWh |  |  | SPA |  |  | used
1135 | Eextra_total H | Extra inverter PowerTOUser_Extra total(high) | [9 empty] | 0.1kWh |  |  | SPA |  |  | used
1136 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) | [9 empty] | 0.1kWh |  |  | SPA |  |  | used
1137 | Esystem_today H | System electric energy today H | [9 empty] | 0.1kWh |  |  | SPA used System electric energy today H
1138 | Esystem_ L | System electric energy today L | [9 empty] | 0.1kWh |  |  | SPA used System electric energy today L
1139 | Esystem_total H | System electric energy total H | [9 empty] | 0.1kWh |  |  | SPA used System electric energy total H
1140 | Esystem_ total L | System electric energy total L | [9 empty] | 0.1kWh |  |  | SPA used System electric energy total L
1141 | Eself_today H | self electric energy today H | [9 empty] | 0.1kWh |  |  | self electric energy today H
1142 | Eself_ today L | self electric energy today L | [9 empty] | 0.1kWh |  |  | self electric energy today L
1143 | Eself_total H | self electric energy total H | [9 empty] | 0.1kWh |  |  | self electric energy total H
1144 | Eself_ total L | self electric energy total L | [9 empty] | 0.1kWh |  |  | self electric energy total L
1145 | PSystem H | System power H | [9 empty] | 0.1w |  |  | System power H
1146 | PSystem L | System power L | [9 empty] | 0.1w |  |  | System power L
1147 | PSelf H | self power H | [9 empty] | 0.1w |  |  | self power H
1148 | PSelf L | self power L | [9 empty] | 0.1w |  |  | self power L
1149 | EPVAll_Today H | PV electric energy today H
1150 | EPVAll_Today L | PV electric energy today L
1151 | AcDischarge PackSn | Discharge number |  |  | power |  | pack | serial | R |  |  | /
1152 |  | Cumulative discharge power high 16-bit byte | [6 empty] | R |  |  |  | 0.1 | kWH
1153 |  | Cumulative discharge power low 16-bit byte | [6 empty] | R |  |  |  | 0.1 | kWH
1154 | AccCharge PackSn | charge power pack serial number | [6 empty] | R |  |  | /
1155 |  | Cumulative charge power high 16-bit byte | [6 empty] | R |  |  |  | 0.1 | kWH
1156 |  | Cumulative charge power low 16-bit byte | [6 empty] | R |  |  |  | 0.1 | kWH
1157 |  |  | FirstBattFaultSn | [5 empty] | R |  |  | /
1158 |  |  | Second BattFaultSn | [5 empty] | R |  |  | /
1159 |  |  | Third BattFaultSn | [5 empty] | R |  |  | /
1160 |  |  | Fourth BattFaultSn | [5 empty] | R |  |  | /
1161 |  |  | Battery history fault code 1 | [5 empty] | R |  |  | /
1162 |  |  | Battery history fault code 2 | [5 empty] | R |  |  | /
1163 |  |  | Battery history fault code 3 | [5 empty] | R |  |  | /
1164 |  |  | Battery history fault code 4 | [5 empty] | R |  |  | /
1165 |  |  | Battery history fault code 5 | [5 empty] | R |  |  | /
1166 |  |  | Battery history fault code 6 | [5 empty] | R |  |  | /
1167 |  |  | Battery history fault code 7 | [5 empty] | R |  |  | /
1168 |  |  | Battery history fault code 8 | [5 empty] | R |  |  | /
1169 |  | Number of battery codes PACK number + BIC forward and reverse codes | [6 empty] | R |  |  | /
1170
…… | / | / | [6 empty] | / |  |  | / |  |  | reversed
1199 | NewEPowerCalc Flag | Intelligent reading is used to identify software compatibility features | [12 empty] | 0 ： Old energy calculation； 1 ： new energy calculation
1200 | MaxCellVolt | Maximum cell voltage | [6 empty] | R |  |  | 0.001V
1201 | MinCellVolt | Minimum cell voltage | [6 empty] | R |  |  | 0.001V
1202 | ModuleNum | Number of Battery modules | [6 empty] | R |  |  | /
1203 | TotalCellNum | Total number of cells | [6 empty] | R |  |  | /
1204 | MaxVoltCellNo | MaxVoltCellNo | [6 empty] | R |  |  | /
1205 | MinVoltCellNo | MinVoltCellNo | [6 empty] | R |  |  | /
1206 | MaxTemprCell_ 10T | MaxTemprCell_10T | [6 empty] | R |  |  | 0.1℃
1207 | MinTemprCell_1 0T | MinTemprCell_10T | [6 empty] | R |  |  | 0.1℃
1208 | MaxTemprCellN o | MaxTemprCellNo | [6 empty] | R |  |  | /
1209 | MinTemprCellN o | MinTemprCellNo | [6 empty] | R |  |  | /
1210 | ProtectPackID | Fault Pack ID | [6 empty] | R |  |  | /
1211 | MaxSOC | Parallel maximum SOC | [6 empty] | R |  |  | 1%
1212 | MinSOC | Parallel minimum SOC | [6 empty] | R |  |  | 1%
1213 | BatProtect1Add | BatProtect1Add | [6 empty] | R |  |  | /
1214 | BatProtect2Add | BatProtect2Add | [6 empty] | R |  |  | /
1215 | BatWarn1Add | BatWarn1Add | [6 empty] | R |  |  | /
1216 | BMS_HighestSof tVersion | BMS_HighestSoftVersion | [6 empty] | R |  |  | /
1217 | BMS_Hardware Version | BMS_HardwareVersion | [6 empty] | R |  |  | /
1218 | BMS_RequestTy pe | BMS_RequestType | [6 empty] | R |  |  | /
…… | / | / | [6 empty] | / |  |  | / |  |  | reversed
1248 | bKeyAgingTestO kFlag | Success sign of key detection before aging | [12 empty] | 1：Finished test 0 ： test not completed
1249 | / | / | [6 empty] | / |  |  | / |  |  | reversed
2000 | Inverter Status | Inverter run state | [7 empty] | 0:waiting, 1:normal, 3:fault | [6 empty] | SPA
…… | reversed
2035 | Pac H | Output power (high) | [11 empty] | 0.1W |  |  | SPA
2036 | Pac L | Output power (low) | [11 empty] | 0.1W |  |  | SPA
2037 | Fac | Grid frequency | [11 empty] | 0.01Hz |  |  | SPA
2038 | Vac1 | Three/single phase grid voltage | [11 empty] | 0.1V |  |  | SPA
2039 | Iac1 | Three/single phase grid output current | [11 empty] | 0.1A |  |  | SPA
2040 | Pac1 H | Three/single phase grid output watt VA (high) | [11 empty] | 0.1VA |  |  | SPA
2041 | Pac1 L | Three/single phase grid output watt VA(low) | [11 empty] | 0.1VA |  |  | SPA
…… | reversed
2053 | Eac today H | Today generate energy (high) | [11 empty] | 0.1kWH |  |  | SPA
2054 | Eac today L | Today generate energy (low) | [11 empty] | 0.1kWH |  |  | SPA
2055 | Eac total H | Total generate energy (high) | [11 empty] | 0.1kWH |  |  | SPA
2056 | Eac total L | Total generate energy (low) | [11 empty] | 0.1kWH |  |  | SPA
2057 | Time total H | Work time total (high) | [11 empty] | 0.5s |  |  | SPA
2058 | Time total L | Work time total (low) | [11 empty] | 0.5s |  |  | SPA
…… | reversed
2093 | Temp1 | Inverter temperature | [11 empty] | 0.1C |  |  | SPA
2094 | Temp2 | The inside IPM in inverter Temperature | [11 empty] | 0.1C |  |  | SPA
2095 | Temp3 | Boost temperature | [11 empty] | 0.1C |  |  | SPA
2096 | Temp4 | [15 empty] | reserved
2097 | uwBatVolt_DSP | BatVolt_DSP | [11 empty] | 0.1V |  |  | BatVolt(DSP)
2098 | P Bus Voltage | P Bus inside Voltage | [11 empty] | 0.1V |  |  | SPA
2099 | N Bus Voltage | N Bus inside Voltage | [11 empty] | 0.1V |  |  | SPA
2100 | RemoteCtrlEn | / | [7 empty] | 0.Load First 1.BatFirst 2.Grid |  |  |  | / |  |  | Remote setup enable
2101 | RemoteCtrlPow er | / | [11 empty] | / |  |  | Remotely set power
2102 | Extra AC Power to grid_H | Extra inverte AC Power to grid High | [7 empty] | For SPA connect inverter | [6 empty] | SPA used
2103 | Extra AC Power to grid_L | Extrainverte AC Power to grid Low | [14 empty] | SPA used
2104 | Eextra_today H | Extra inverter PowerTOUser_Extra today (high) | [7 empty] | R |  |  |  | 0.1kWh |  |  | SPA |  | used
2105 | Eextra_today L | Extra inverter PowerTOUser_Extra today (low) | [7 empty] | R |  |  |  | 0.1kWh |  |  | SPA |  | used
2106 | Eextra_total H | Extra inverter PowerTOUser_Extratotal(high) | [11 empty] | 0.1kWh |  |  | SPA |  | used
2107 | Eextra_total L | Extra inverter PowerTOUser_Extra total(low) | [11 empty] | 0.1kWh |  |  | SPA |  | used
2108 | Esystem_today H | System electric energy today H | [11 empty] | 0.1kWh |  |  | SPA used System electric energy today H
2109 | Esystem_ L | System electric energy today L | [11 empty] | 0.1kWh |  |  | SPA used System electric energy today L
2110 | Esystem_total H | System electric energy total H | [11 empty] | 0.1kWh |  |  | SPA used System
electric energy total H
2111 | Esystem_ total L | System electric energy total L | [11 empty] | 0.1kWh |  |  | SPA used System electric energy total L
2112 | EACharge_Today _H | ACCharge energy today | [11 empty] | 0.1kwh |  |  | Storage Power
2113 | EACharge_Today _L | ACCharge energy today | [11 empty] | 0.1kwh |  |  | Storage Power
2114 | EACharge_Total _H | ACCharge energy total | [11 empty] | 0.1kwh |  |  | Storage Power
2115 | EACharge_Total _L | ACCharge energy total | [11 empty] | 0.1kwh |  |  | Storage Power
2116 | AC charge Power_H | Grid power to local load | [11 empty] | 0.1kwh |  |  | Storage Power
2117 | AC charge Power_L | Grid power to local load | [11 empty] | 0.1kwh |  |  | Storage Power
2118 | Priority | 0:Load First 1:Battery First 2:Grid First | [14 empty] | Storage Power
2119 | Battery Type | 0：Lead-acid 1：Lithium battery | [14 empty] | Storage Power
2120 | AutoProofreadC MD | Aging mode | [14 empty] | Storage Power
… | reserved | [15 empty] | reserved
2124 | reserved | [15 empty] | reserved
Use for TL-X and TL-XH
3000 | Inverter Status | Inverter run state High 8 bits mode (specific mode) 0: Waiting module 1: Self-test mode, optional 2: Reserved 3：SysFault module 4: Flash module 5：PVBATOnline module: 6：BatOnline module
7：PVOfflineMode 8：BatOfflineMode The lower 8 bits indicate the machine status (web page display) 0: StandbyStatus; 1: NormalStatus; 3: FaultStatus 4：FlashStatus;
3001 | Ppv H | PV total power | [11 empty] | 0.1W
3002 | Ppv L
3003 | Vpv1 | PV1 voltage | [11 empty] | 0.1V
3004 | Ipv1 | PV1 input current | [11 empty] | 0.1A
3005 | Ppv1 H | PV1 power | [11 empty] | 0.1W
3006 | Ppv1 L
3007 | Vpv2 | PV2 voltage | [11 empty] | 0.1V
3008 | Ipv2 | PV2 input current | [11 empty] | 0.1A
3009 | Ppv2 H | PV2 power | [11 empty] | 0.1W
3010 | Ppv2 L
3011 | Vpv3 | PV3 voltage | [11 empty] | 0.1V
3012 | Ipv3 | PV3 input current | [11 empty] | 0.1A
3013 | Ppv3 H | PV3 power | [11 empty] | 0.1W
3014 | Ppv3 L
3015 | Vpv4 | PV4 voltage
3016 | Ipv4 | PV4 input current
3017 | Ppv4H | PV4 power
3018 | Ppv4L
3019 | Psys H | System output power | [11 empty] | 0.1W
3020 | Psys L
3021 | Qac H | reactive power | [11 empty] | 0.1Var
3022 | Qac L
3023 | Pac H | Output power | [11 empty] | 0.1W |  | Output power
3024 | Pac L
3025 | Fac | Grid frequency | [11 empty] | 0.01Hz |  | Grid frequency
3026 | Vac1 | Three/single phase grid voltage | [11 empty] | 0.1V |  | Three/single phase grid voltage
3027 | Iac1 | Three/single phase grid output current | [11 empty] | 0.1A |  | Three/single
phase grid output current
3028 | Pac1 H | Three/single phase grid output watt VA | [11 empty] | 0.1VA |  | Three/single phase grid output watt VA
3029 | Pac1 L
3030 | Vac2 | Three phase grid voltage | [11 empty] | 0.1V |  | Three phase grid voltage
3031 | Iac2 | Three phase grid output current | [11 empty] | 0.1A |  | Three phase grid output current
3032 | Pac2 H | Three phase grid output power | [11 empty] | 0.1VA |  | Three phase grid output power
3033 | Pac2 L
3034 | Vac3 | Three phase grid voltage | [11 empty] | 0.1V |  | Three phase grid voltage
3035 | Iac3 | Three phase grid output current | [11 empty] | 0.1A |  | Three phase grid output current
3036 | Pac3 H | Three phase grid output power | [11 empty] | 0.1VA |  | Three phase grid output power
3037 | Pac3 L
3038 | Vac_RS | Three phase grid voltage | [11 empty] | 0.1V
3039 | Vac_ST | Three phase grid voltage | [11 empty] | 0.1V
3040 | Vac_TR | Three phase grid voltage | [11 empty] | 0.1V
3041 | Ptouser total H | Total forward power | [11 empty] | 0.1W |  | Total forward power
3042 | Ptouser total L
3043 | Ptogrid total H | Total reverse power | [11 empty] | 0.1W |  | Total reverse power
3044 | Ptogrid total L
3045 | Ptoload total H | Total load power | [11 empty] | 0.1W |  | Total load power
3046 | Ptoload total L
3047 | Time total H | Work time total | [11 empty] | 0.5s
3048 | Time total L
3049 | Eac today H | Today generate energy | [11 empty] | 0.1kWh |  | Today generate energy
3050 | Eac today L
3051 | Eac total H | Total generate energy | [11 empty] | 0.1kWh |  | Total generate
3052 | Eac total L
energy
3053 | Epv_total H | PV energy total | [11 empty] | 0.1kWh |  | PV energy total
3054 | Epv_total L
3055 | Epv1_today H | PV1 energy today | [11 empty] | 0.1kWh
3056 | Epv1_today L
3057 | Epv1_total H | PV1 energy total | [11 empty] | 0.1kWh
3058 | Epv1_total L
3059 | Epv2_today H | PV2 energy today | [11 empty] | 0.1kWh
3060 | Epv2_today L
3061 | Epv2_total H | PV2 energy total | [11 empty] | 0.1kWh
3062 | Epv2_total L
3063 | Epv3_today H | PV3 energy today | [11 empty] | 0.1kWh
3064 | Epv3_today L
3065 | Epv3_total H | PV3 energy total | [11 empty] | 0.1kWh
3066 | Epv3_total L
3067 | Etouser_today H | Today energy to user | [11 empty] | 0.1kWh |  | Today energy to user
3068 | Etouser_today L
3069 | Etouser_total H | Total energy to user | [11 empty] | 0.1kWh |  | Total energy to user
3070 | Etouser_total L
3071 | Etogrid_today H | Today energy to grid | [11 empty] | 0.1kWh |  | Today energy to grid
3072 | Etogrid_today L
3073 | Etogrid_total H | Total energy to grid | [11 empty] | 0.1kWh |  | Total energy to grid
3074 | Etogrid_total L
3075 | Eload_today H | Today energy of user load | [11 empty] | 0.1kWh |  | Today energy of user load
3076 | Eload_today L
3077 | Eload_total H | Total energy of user load | [11 empty] | 0.1kWh |  | Total energy of user load
3078 | Eload_total L
3079 | Epv4_today H | PV4 energy today | [11 empty] | 0.1kWh
3080 | Epv4_today L
3081 | Epv4_total H | PV4 energy total | [11 empty] | 0.1kWh
3082 | Epv4_total L
3083 | Epv_today H | PV energy today | [11 empty] | 0.1kWh
3084 | Epv_today L
3085 | Reserved
3086 | DeratingMode | DeratingMode | [13 empty] | 0:cNOTDerate 1:cPVHighDer ate 2: cPowerCon stantDerate 3: cGridVHigh Derate 4:cFreqHighD erate 5:cDcSoureM odeDerate 6:cInvTemprD erate 7:cActivePow erOrder 8:cLoadSpeed Process 9:cOverBack byTime 10:cInternalT emprDerate 11:cOutTemp rDerate 12:cLineImpe CalcDerate 13: cParallelA ntiBackflowD erate 14:cLocalAnti BackflowDera te 15:cBdcLoadP riDerate 16:cChkCTErr Derate
3087 | ISO | PV ISO value | [11 empty] | 1KΩ
3088 | DCI_R | R DCI Curr | [11 empty] | 0.1mA
3089 | DCI_S | S DCI Curr | [11 empty] | 0.1mA
3090 | DCI_T | T DCI Curr | [11 empty] | 0.1mA
3091 | GFCI | GFCI Curr | [11 empty] | 1mA
3092 | Bus Voltage | total bus voltage | [11 empty] | 0.1V
3093 | Temp1 | Inverter temperature | [11 empty] | 0.1℃
3094 | Temp2 | The inside IPM in inverter temperature | [11 empty] | 0.1℃
3095 | Temp3 | Boost temperature | [11 empty] | 0.1℃
3096 | Temp4 | Reserved | [11 empty] | 0.1℃
3097 | Temp5 | Commmunication broad temperature | [11 empty] | 0.1℃
3098 | P Bus Voltage | P Bus inside Voltage | [11 empty] | 0.1V
3099 | N Bus Voltage | N Bus inside Voltage | [11 empty] | 0.1V
3100 | IPF | Inverter output PF now | [13 empty] | 0-20000
3101 | RealOPPercent | Real Output power Percent | [11 empty] | 1% |  | 1~100
3102 | OPFullwatt H | Output Maxpower Limited | [11 empty] | 0.1W |  | Output Maxpower Limited
3103 | OPFullwatt L
3104 | StandbyFlag | Inverter standby flag | [11 empty] | bitfield |  | bit0:turn off Order； bit1:PV Low； bit2:AC Volt/Freq out of scope； bit3~bit7 ： Reserved
3105 | Fault Maincode | Inverter fault maincode
3106 | Warn Maincode | Inverter Warning maincode
3107 | Fault Subcode | Inverter fault subcode | [11 empty] | bitfield
3108 | Warn Subcode | Inverter Warning subcode | [11 empty] | bitfield
3109 | [13 empty] | bitfield
3110 | [13 empty] | bitfield
3111 | uwPresentFFTVa lue [CHANNEL_A ] | PresentFFTValue [CHANNEL_A] | [11 empty] | bitfield
3112 | bAfciStatus | AFCI Status | [13 empty] | 0 ： waiting state 1：self-check 2 ： Detection of arcing state 3：fault state 4 ： update state
3113 | uwStrength[CHA NNEL_A] | AFCI Strength[CHANNEL_A]
3114 | uwSelfCheckVal ue[CHANNEL_A] | AFCI SelfCheck[CHANNEL_A]
3115 | inv start delay time | inv start delay time | [11 empty] | 1S |  | inv start delay time
3116 | Reserved
3117 | Reserved
3118 | BDC_OnOffState | BDC connect state | [13 empty] | 0:No BDC Connect 1:BDC1 Connect 2:BDC2 Connect 3:BDC1+BDC2 Connect
3119 | DryContactState | Current status of DryContact | [13 empty] | Current status of DryContact 0: turn off; 1: turn on;
3120 | Reserved
3121 | Pself H | self-use power | [11 empty] | 0.1W
3122 | Pself L
3123 | Esys_today H | System energy today | [11 empty] | 0.1kwh
3124 | Esys_today L
3125 | Edischr_today H | Today discharge energy | [11 empty] | 0.1kWh |  | Today discharge energy
3126 | Edischr_today L
3127 | Edischr_total H | Total discharge energy | [11 empty] | 0.1kWh |  | Total discharge energy
3128 | Edischr_total L
3129 | Echr_today H | Charge energy today | [11 empty] | 0.1kWh |  | Charge energy today
3130 | Echr_today L
3131 | Echr_total H | Charge energy total | [11 empty] | 0.1kWh |  | Charge energy total
3132 | Echr_total L
3133 | Eacchr_today H | Today energy of AC charge | [11 empty] | 0.1kWh |  | Today energy of AC charge
3134 | Eacchr_today L
3135 | Eacchr_total H | Total energy of AC charge | [11 empty] | 0.1kWh |  | Total energy of AC charge
3136 | Eacchr_total L
3137 | Esys_total H
3138 | Esys_total L | Total energy of system output \ | [11 empty] | 0.1kWh
3139 | Eself_today H | Today energy of Self output | [11 empty] | 0.1kWh
3140 | Eself_today L
3141 | Eself_total H | Total energy of Self output | [11 empty] | 0.1kwh
3142 | Eself_ total L
3143 | Reserved
3144 | Priority | Word Mode | [13 empty] | 0 LoadFirst 1 BatteryFirs t 2 GridFirst
3145 | EPS Fac | UPS frequency | [11 empty] | 0.01Hz
3146 | EPS Vac1 | UPS phase R output voltage | [11 empty] | 0.1V
3147 | EPS Iac1 | UPS phase R output current | [11 empty] | 0.1A
3148 | EPS Pac1 H | UPS phase R output power | [11 empty] | 0.1VA
3149 | EPS Pac1 L
3150 | EPS Vac2 | UPS phase S output voltage | [11 empty] | 0.1V
3151 | EPS Iac2 | UPS phase S output current | [11 empty] | 0.1A
3152 | EPS Pac2 H | UPS phase S output power | [11 empty] | 0.1VA
3153 | EPS Pac2 L
3154 | EPS Vac3 | UPS phase T output voltage | [11 empty] | 0.1V
3155 | EPS Iac3 | UPS phase T output current | [11 empty] | 0.1A
3156 | EPS Pac3 H | UPS phase T output power | [11 empty] | 0.1VA
3157 | EPS Pac3 L
3158 | EPS Pac H | UPS output power | [11 empty] | 0.1VA
3159 | EPS Pac L
3160 | Loadpercent | Load percent of UPS ouput | [11 empty] | 0.1%
3161 | PF | Power factor | [11 empty] | 0.1
3162 | DCV | DC voltage | [11 empty] | 1mV
3163 | Reserved
3164 | NewBdcFlag | Whether to parse BDC data separately | [13 empty] | 0: Don't need 1：need
3165 | BDCDeratingMo de | BDCDeratingMode： 0: Normal, unrestricted 1：Standby or fault 2：Maximum battery current limit (discharge) 3：Battery discharge Enable (Discharge) 4：High bus discharge derating
(discharge) 5：High temperature discharge derating (discharge) 6：System warning No discharge (discharge) 7-15 Reserved (Discharge) 16：Maximum charging current of battery (charging) 17：High Temperature (LLC and Buckboost) (Charging) 18：Final soft charge 19：SOC setting limits (charging) 20：Battery low temperature (charging) 21：High bus voltage (charging) 22：Battery SOC (charging) 23: Need to charge (charge） 24: System warning not charging (charging) 25-29：Reserve (charge)
3166 | SysState_Mode | System work State and mode The upper 8 bits indicate the mode; 0：No charge and discharge； 1：charge； 2：Discharge； The lower 8 bits represent the status; 0: StandbyStatus; 1: NormalStatus; 2: FaultStatus 3：FlashStatus; | [13 empty] | BDC1
3167 | FaultCode | Storge device fault code
3168 | WarnCode | Storge device warning code
3169 | Vbat | Battery voltage | [11 empty] | 0.01V
3170 | Ibat | Battery current | [11 empty] | 0.1A
3171 | SOC | State of charge Capacity | [11 empty] | 1%
3172 | Vbus1 | Total BUS voltage | [11 empty] | 0.1V
3173 | Vbus2 | On the BUS voltage | [11 empty] | 0.1V
3174 | Ibb | BUCK-BOOST Current | [11 empty] | 0.1A
3175 | Illc | LLC Current | [11 empty] | 0.1A
3176 | TempA | Temperture A | [11 empty] | 0.1℃
3177 | TempB | Temperture B | [11 empty] | 0.1℃
3178 | Pdischr H | Discharge power | [11 empty] | 0.1W
3179 | Pdischr L
3180 | Pchr H | Charge power | [11 empty] | 0.1W
3181 | Pchr L
3182 | Edischr_total H | Discharge total energy of storge device | [11 empty] | 0.1kWh
3183 | Edischr_total L
3184 | Echr_total H | Charge total energy of storge device | [11 empty] | 0.1kWh
3185 | Echr_total L
3186 | Reserved | Reserved
3187 | BDC1_Flag | BDC mark (charge and discharge, fault alarm code) Bit0: ChargeEn; BDC allows charging Bit1: DischargeEn; BDC allows discharge Bit2~7: Resvd; reserved Bit8~11: WarnSubCode; BDC sub-warning code Bit12~15: FaultSubCode; BDC sub-error code
3188 | Vbus2 | Lower BUS voltage | [11 empty] | 0.1V
3189 | BmsMaxVoltCell No | BmsMaxVoltCellNo
3190 | BmsMinVoltCell No | BmsMinVoltCellNo
3191 | BmsBatteryAvgT emp | BmsBatteryAvgTemp
3192 | BmsMaxCellTem p | BmsMaxCellTemp | [11 empty] | 0.1°C
3193 | BmsBatteryAvgT emp | BmsBatteryAvgTemp | [11 empty] | 0.1°C
3194 | BmsMaxCellTem p | BmsMaxCellTemp
3195 | BmsBatteryAvgT emp | BmsBatteryAvgTemp
3196 | BmsMaxSOC | BmsMaxSOC | [11 empty] | 1%
3197 | BmsMinSOC | BmsMinSOC | [11 empty] | 1%
3198 | ParallelBatteryN um | ParallelBatteryNum
3199 | BmsDerateReas on | BmsDerateReason
3200 | BmsGaugeFCC （Ah） | BmsGaugeFCC（Ah）
3201 | BmsGaugeRM （Ah） | BmsGaugeRM（Ah）
3202 | BmsError | BMS Protect1
3203 | BmsWarn | BMSWarn1
3204 | BmsFault | BMS Fault1
3205 | BmsFault2 | BMS Fault2
3206 | Reserved
3207 | Reserved
3208 | Reserved
3209 | Reserved
3210 | BatIsoStatus | Battery ISO detection status | [13 empty] | 0：Not detected 1 ： Detection completed
3211 | BattNeedCharge RequestFlag | battery work request | [11 empty] | bit0:1： Prohibit chargin g，0： Allow the chargin g bit1:1： Enable strong charge， 0： disable strong charge bit2:1： Enable strong charge2 0： disable strong charge
2 bit8:1: Dischar ge is prohibit ed， 0： allow discharg e bit9:1： Turn on power reductio n 0： turn off power reductio n；
3212 | BMS_Status | battery working status | [7 empty] | R | [5 empty] | 0: dormancy 1:Charge 2:Discharge 3:free 4:standby 5:Soft start 6:fault 7:update
3213 | BmsError2 | BMS Protect2 | [7 empty] | R |  |  |  | 1
3214 | BmsWarn2 | BMS Warn2 | [7 empty] | R |  |  |  | 1
3215 | BMS_SOC | BMS SOC | [7 empty] | R |  |  |  | 1%
3216 | BMS_BatteryVol t | BMS BatteryVolt | [7 empty] | R |  |  |  | 0.01V
3217 | BMS_BatteryCur r | BMS BatteryCurr | [7 empty] | R |  |  |  | 0.01A
3218 | BMS_BatteryTe mp | battery cell maximum temperature | [7 empty] | R |  |  |  | 0.1℃
3219 | BMS_MaxCurr | Maximum charging current | [7 empty] | R |  |  |  | 0.01A
3220 | BMS_MaxDischr Curr | Maximum discharge current | [7 empty] | R |  |  |  | 0.01A
3221 | BMS_CycleCnt | BMSCycleCnt | [7 empty] | R |  |  |  | 1
3222 | BMS_SOH | BMS SOH | [7 empty] | R |  |  |  | 1
3223 | BMS_ChargeVol tLimit | Battery charging voltage limit value | [7 empty] | R |  |  |  | 0.01V
3224 | BMS_Discharge VoltLimit | Battery discharge voltage limit value
3225 | Bms Warn3 | BMS Warn 3 | [7 empty] | R |  |  |  | 1
3226 | Bms Error3 | BMS Protect3 | [7 empty] | R |  |  |  | 1
3227 | Reserved
3228 | Reserved
3229 | Reserved
3230 | BMSSingleVoltM ax | BMS Battery SingleVoltMax | [7 empty] | R |  |  |  | 0.001V
3231 | BMSSingleVoltM in | BMS Battery SingleVoltMin | [7 empty] | R |  |  |  | 0.001V
3232 | BatLoadVolt | Battery LoadVolt | [7 empty] | R |  |  |  | 0.01V |  | [0，650.00]
3233
3234 | Debug data1 | Debug data1 | [7 empty] | R
3235 | Debug data2 | Debug data2 | [7 empty] | R
3236 | Debug data3 | Debug data3 | [7 empty] | R
3237 | Debug data4 | Debug data4 | [7 empty] | R
3238 | Debug data5 | Debug data5 | [7 empty] | R
3239 | Debug data6 | Debug data6 | [7 empty] | R
3240 | Debug data7 | Debug data7 | [7 empty] | R
3241 | Debug data8 | Debug data8 | [7 empty] | R
3242 | Debug data9 | Debug data9 | [7 empty] | R
3243 | Debug data10 | Debug data10 | [7 empty] | R
3244 | Debug data10 | Debug data10 | [7 empty] | R
3245 | Debug data12 | Debug data12 | [7 empty] | R
3246 | Debug data13 | Debug data13 | [7 empty] | R
3247 | Debug data14 | Debug data14 | [7 empty] | R
3248 | Debug data15 | Debug data15 | [7 empty] | R
3249 | Debug data16 | Debug data16 | [7 empty] | R
3250 | Pex1H | PV inverter 1 output power H | [7 empty] | R |  |  |  | 0.1W
3251 | Pex1L | PV inverter 1 output power L | [7 empty] | R |  |  |  | 0.1W
3252 | Pex2H | PV inverter 2 output power H | [7 empty] | R |  |  |  | 0.1W
3253 | Pex2L | PV inverter 2 output power L | [7 empty] | R |  |  |  | 0.1W
3254 | Eex1TodayH | PV inverter 1 energy Today H | [7 empty] | R |  |  |  | 0.1kWh
3255 | Eex1TodayL | PV inverter 1 energy Today L | [7 empty] | R |  |  |  | 0.1kWh
3256 | Eex2TodayH | PV inverter 2 energy Today H | [7 empty] | R |  |  |  | 0.1kWh
3257 | Eex2TodayL | PV inverter 2 energy Today L | [7 empty] | R |  |  |  | 0.1kWh
3258 | Eex1TotalH | PV inverter 1 energy Total H | [7 empty] | R |  |  |  | 0.1kWh
3259 | Eex1TotalL | PV inverter 1 energy Total L | [7 empty] | R |  |  |  | 0.1kWh
3260 | Eex2TotalH | PV inverter 2 energy Total H | [7 empty] | R |  |  |  | 0.1kWh
3261 | Eex2TotalL | PV inverter 2 energy Total L | [7 empty] | R |  |  |  | 0.1kWh
3262 | uwBatNo | battery pack number | [7 empty] | R | [5 empty] | BDC reports are updated every 15 minutes
3263 | BatSerialNum1 | Battery pack serial numberSN[0]SN[1] | [7 empty] | R | [5 empty] | BDC reports are updated every 15 minutes
3264 | BatSerialNum2 | Battery pack serial numberSN[2]SN[3] | [7 empty] | R
3265 | BatSerialNum3 | Battery pack serial numberSN[4]SN[5] | [7 empty] | R
3266 | BatSerialNum4 | Battery pack serial numberSN[6]SN[7] | [7 empty] | R
3267 | BatSerialNum5 | Battery pack serial numberSN[8]SN[9] | [7 empty] | R
3268 | BatSerialNum6 | Battery pack serial numberSN[10]SN[11] | [7 empty] | R
3269 | BatSerialNum7 | Battery pack serial numberSN[12]SN[13] | [7 empty] | R
3270 | BatSerialNum8 | Battery pack serial numberSN[14]SN[15] | [7 empty] | R
3271- 3279 | Reserve | Reserve
3280 | bClrTodayDataFl ag | Clear day data flag | [7 empty] | R | [5 empty] | Data of the current day that the server
determines whether to clear. 0:not cleared. 1: Clear.
BDC and BMS information (support up to 10 PARALLEL BDCS)
4000- 4107 | 1 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4108- 4215 | 2 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
…… |  | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4864- 4971 | 9 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).
4972- 5079 | 10 | The first 8 registers are the 16-bit serial number of BDC, then 69 registers have the same data area as 3165-3233, the remaining 31 registers are reserved, a total of 108 registers (including 8 registers occupied by serial number).